## Aqua_Param
No. | Parameter name | Aqua | HVAC | Group | Number | SDO Access |  | BUS Mapping | Serial (hex) | Serial (dec+1) | Data Format
[6 empty] | Index (hex) | Sub (hex) |  |  |  | BUS | Format
F00 | Data Protection | ✔ | ✔ | F | 00 | 5F04 | 01 | 0400 | 0000 | 1 | All | 1
F01 | Frequency Command 1 | ✔ | ✔ | F | 01 | 5F04 | 02 | 0401 | 0001 | 2 | All | 1
F02 | Operation Method | ✔ | ✔ | F | 02 | 5F04 | 03 | 0402 | 0002 | 3 | All | 1
F03 | Maximum Frequency 1 | ✔ | ✔ | F | 03 | 5F04 | 04 | 0403 | 0003 | 4 | All | 3
F04 | Base Frequency 1 | ✔ | ✔ | F | 04 | 5F04 | 05 | 0404 | 0004 | 5 | All | 3
F05 | Rated Voltage at Base Frequency 1 | ✔ | ✔ | F | 05 | 5F04 | 06 | 0405 | 0005 | 6 | All | 1
F06 | Maximum Output Voltage 1 | ✔ | ✔ | F | 06 | 5F04 | 07 | 0406 | 0006 | 7 | All | 1
F07 | Acceleration Time 1 | ✔ | ✔ | F | 07 | 5F04 | 08 | 0407 | 0007 | 8 | All | 12
F08 | Deceleration Time 1 | ✔ | ✔ | F | 08 | 5F04 | 09 | 0408 | 0008 | 9 | All | 12
F09 | Torque Boost 1 | ✔ | ✔ | F | 09 | 5F04 | 0A | 0409 | 0009 | 10 | All | 3
F10 | Electronic Thermal 1 (Select motor characteristics) | ✔ | ✔ | F | 10 | 5F04 | 0B | 040A | 000A | 11 | All | 1
F11 | Electronic Thermal 1 (Overload detection level) | ✔ | ✔ | F | 11 | 5F04 | 0C | 040B | 000B | 12 | FGI | 24
F11 | Electronic Thermal 1 (Overload detection level) | ✔ | ✔ | F | 11 | 5F04 | 0C | 040B | 000B | 12 | RTU | 19
F11 | Electronic Thermal 1 (Overload detection level) | ✔ | ✔ | F | 11 | 5F04 | 0C | 040B | 000B | 12 | BUS | 24
F12 | Electronic Thermal 1 (Thermal time constant) | ✔ | ✔ | F | 12 | 5F04 | 0D | 040C | 000C | 13 | All | 3
F14 | Restart Mode after Momentary Power Failure (Mode selection) | ✔ | ✔ | F | 14 | 5F04 | 0F | 040E | 000E | 15 | All | 1
F15 | Frequency Limiter (High) | ✔ | ✔ | F | 15 | 5F04 | 10 | 040F | 000F | 16 | All | 3
F16 | Frequency Limiter (Low) | ✔ | ✔ | F | 16 | 5F04 | 11 | 0410 | 0010 | 17 | All | 3
F18 | Bias (Frequency command 1) | ✔ | ✔ | F | 18 | 5F04 | 13 | 0412 | 0012 | 19 | All | 6
F20 | DC Braking 1 (Braking starting frequency) | ✔ | ✔ | F | 20 | 5F04 | 15 | 0414 | 0014 | 21 | All | 3
F21 | DC Braking 1 (Braking level) | ✔ | ✔ | F | 21 | 5F04 | 16 | 0415 | 0015 | 22 | All | 1
F22 | DC Braking 1 (Braking time) | ✔ | ✔ | F | 22 | 5F04 | 17 | 0416 | 0016 | 23 | All | 5
F23 | Starting Frequency 1 | ✔ | ✔ | F | 23 | 5F04 | 18 | 0417 | 0017 | 24 | All | 3
F24 | Starting Frequency 1 (Holding time) | ✔ | ✔ | F | 24 | 5F04 | 19 | 0418 | 0018 | 25 | All | 5
F25 | Stop Frequency | ✔ | ✔ | F | 25 | 5F04 | 1A | 0419 | 0019 | 26 | All | 3
F26 | Motor Sound (Carrier frequency) | ✔ | ✔ | F | 26 | 5F04 | 1B | 041A | 001A | 27 | All | 1
F27 | Motor Sound (Tone) | ✔ | ✔ | F | 27 | 5F04 | 1C | 041B | 001B | 28 | All | 1
F29 | Analog Output [FM 1] (Mode selection) | ✔ | ✔ | F | 29 | 5F04 | 1E | 041D | 001D | 30 | All | 1
F30 | Analog Output [FM 1] (Voltage adjustment) | ✔ | ✔ | F | 30 | 5F04 | 1F | 041E | 001E | 31 | All | 1
F31 | Analog Output [FM 1] (Function) | ✔ | ✔ | F | 31 | 5F04 | 20 | 041F | 001F | 32 | All | 1
F32 | Analog Output [FM 2] (Mode selection) | ✔ | ✔ | F | 32 | 5F04 | 21 | 0420 | 0020 | 33 | All | 1
F34 | Analog Output [FM 2] (Voltage adjustment) | ✔ | ✔ | F | 34 | 5F04 | 23 | 0422 | 0022 | 35 | All | 1
F35 | Analog Output [FM2] (Function) | ✔ | ✔ | F | 35 | 5F04 | 24 | 0423 | 0023 | 36 | All | 1
F37 | Load Selection/Auto Torque Boost/Auto Energy Saving Operation 1 | ✔ | ✔ | F | 37 | 5F04 | 26 | 0425 | 0025 | 38 | All | 1
F40 | Torque Limiter 1-1 | ✔ | ✔ | F | 40 | 5F04 | 29 | 0428 | 0028 | 41 | All | 1
F41 | Torque Limiter 1-2 | ✔ | ✔ | F | 41 | 5F04 | 2A | 0429 | 0029 | 42 | All | 1
F42 | Drive Control Selection 1 | ✔ | ✔ | F | 42 | 5F04 | 2B | 042A | 002A | 43 | All | 1
F43 | Current Limiter (Mode selection) | ✔ | ✔ | F | 43 | 5F04 | 2C | 042B | 002B | 44 | All | 1
F44 | Current Limiter (Level) | ✔ | ✔ | F | 44 | 5F04 | 2D | 042C | 002C | 45 | All | 1
E01 | Terminal [X1] Function | ✔ | ✔ | E | 01 | 5F05 | 02 | 0501 | 0101 | 258 | All | 1
E02 | Terminal [X2] Function | ✔ | ✔ | E | 02 | 5F05 | 03 | 0502 | 0102 | 259 | All | 1
E03 | Terminal [X3] Function | ✔ | ✔ | E | 03 | 5F05 | 04 | 0503 | 0103 | 260 | All | 1
E04 | Terminal [X4] Function | ✔ | ✔ | E | 04 | 5F05 | 05 | 0504 | 0104 | 261 | All | 1
E05 | Terminal [X5] Function | ✔ | ✔ | E | 05 | 5F05 | 06 | 0505 | 0105 | 262 | All | 1
E06 | Terminal [X6] Function | ✔ | ✔ | E | 06 | 5F05 | 07 | 0506 | 0106 | 263 | All | 1
E07 | Terminal [X7] Function | ✔ | ✔ | E | 07 | 5F05 | 08 | 0507 | 0107 | 264 | All | 1
E10 | Acceleration Time 2 | ✔ | ✔ | E | 10 | 5F05 | 0B | 050A | 010A | 267 | All | 12
E11 | Deceleration Time 2 | ✔ | ✔ | E | 11 | 5F05 | 0C | 050B | 010B | 268 | All | 12
E12 | Acceleration Time 3 | ✔ | ✔ | E | 12 | 5F05 | 0D | 050C | 010C | 269 | All | 12
E13 | Deceleration Time 3 | ✔ | ✔ | E | 13 | 5F05 | 0E | 050D | 010D | 270 | All | 12
E14 | Acceleration Time 4 | ✔ | ✔ | E | 14 | 5F05 | 0F | 050E | 010E | 271 | All | 12
E15 | Deceleration Time 4 | ✔ | ✔ | E | 15 | 5F05 | 10 | 050F | 010F | 272 | All | 12
E16 | Torque Limiter 2(Driving) | ✔ | ✔ | E | 16 | 5F05 | 11 | 0510 | 0110 | 273 | All | 1
E17 | Torque Limiter 2(Braking) | ✔ | ✔ | E | 17 | 5F05 | 12 | 0511 | 0111 | 274 | All | 1
E20 | Terminal [Y1] Function | ✔ | ✔ | E | 20 | 5F05 | 15 | 0514 | 0114 | 277 | All | 1
E21 | Terminal [Y2] Function | ✔ | ✔ | E | 21 | 5F05 | 16 | 0515 | 0115 | 278 | All | 1
E22 | Terminal [Y3] Function | ✔ | ✔ | E | 22 | 5F05 | 17 | 0516 | 0116 | 279 | All | 1
E23 | Terminal [Y4] Function | ✔ | ✔ | E | 23 | 5F05 | 18 | 0517 | 0117 | 280 | All | 1
E24 | Terminal [Y5A/C] Function | ✔ | ✔ | E | 24 | 5F05 | 19 | 0518 | 0118 | 281 | All | 1
E27 | Terminal [30A/B/C] Function (Relay output) | ✔ | ✔ | E | 27 | 5F05 | 1C | 051B | 011B | 284 | All | 1
E30 | Frequency Arrival (Hysteresis width) | ✔ | ✔ | E | 30 | 5F05 | 1F | 051E | 011E | 287 | All | 3
E31 | Frequency Detection 1 (Level) | ✔ | ✔ | E | 31 | 5F05 | 20 | 051F | 011F | 288 | All | 3
E32 | Frequency Detection 1 (Hysteresis width) | ✔ | ✔ | E | 32 | 5F05 | 21 | 0520 | 0120 | 289 | All | 3
E34 | Overload Early Warning/Current Detection (Level) | ✔ | ✔ | E | 34 | 5F05 | 23 | 0522 | 0122 | 291 | FGI | 24
E34 | Overload Early Warning/Current Detection (Level) | ✔ | ✔ | E | 34 | 5F05 | 23 | 0522 | 0122 | 291 | RTU | 19
E34 | Overload Early Warning/Current Detection (Level) | ✔ | ✔ | E | 34 | 5F05 | 23 | 0522 | 0122 | 291 | BUS | 24
E35 | Overload Early Warning/Current Detection (Timer) | ✔ | ✔ | E | 35 | 5F05 | 24 | 0523 | 0123 | 292 | All | 5
E37 | Current Detection 2 (Level) | ✔ | ✔ | E | 37 | 5F05 | 26 | 0525 | 0125 | 294 | FGI | 24
E37 | Current Detection 2 (Level) | ✔ | ✔ | E | 37 | 5F05 | 26 | 0525 | 0125 | 294 | RTU | 19
E37 | Current Detection 2 (Level) | ✔ | ✔ | E | 37 | 5F05 | 26 | 0525 | 0125 | 294 | BUS | 24
E38 | Current Detection 2 (Timer) | ✔ | ✔ | E | 38 | 5F05 | 27 | 0526 | 0126 | 295 | All | 5
E61 | Terminal [12] Extended Function | ✔ | ✔ | E | 61 | 5F05 | 3E | 053D | 013D | 318 | All | 1
E62 | Terminal [C1] Extended Function | ✔ | ✔ | E | 62 | 5F05 | 3F | 053E | 013E | 319 | All | 1
E63 | Terminal [V2] Extended Function | ✔ | ✔ | E | 63 | 5F05 | 40 | 053F | 013F | 320 | All | 1
E64 | Saving of Digital Reference Frequency | ✔ | ✔ | E | 64 | 5F05 | 41 | 0540 | 0140 | 321 | All | 1
E65 | Reference Loss Detection (Continuous running frequency) | ✔ | ✔ | E | 65 | 5F05 | 42 | 0541 | 0141 | 322 | All | 1
E80 | Low Torque Detection (Level) | ✔ | ✔ | E | 80 | 5F05 | 51 | 0550 | 0150 | 337 | All | 1
E81 | Low Torque Detection (Timer) | ✔ | ✔ | E | 81 | 5F05 | 52 | 0551 | 0151 | 338 | All | 5
E82 | Switching Frequency of Accel/Decel Time in Low-Speed Domain | ✔ | x | E | 82 | 5F05 | 53 | 0552 | 0152 | 339 | All | 3
E83 | acceleration Time in Low-Speed Domain | ✔ | x | E | 83 | 5F05 | 54 | 0553 | 0153 | 340 | All | 12
E84 | Deceleration Time in Low-Speed Domain | ✔ | x | E | 84 | 5F05 | 55 | 0554 | 0154 | 341 | All | 12
E85 | Gradual Deceleration Time Switching Frequncy | ✔ | x | E | 85 | 5F05 | 56 | 0555 | 0155 | 342 | All | 3
E86 | Gradeal Deceleration Time(Check valve protection) | ✔ | x | E | 86 | 5F05 | 57 | 0556 | 0156 | 343 | All | 12
E98 | Terminal [FWD] Function | ✔ | ✔ | E | 98 | 5F05 | 63 | 0562 | 0162 | 355 | All | 1
E99 | Terminal [REV] Function | ✔ | ✔ | E | 99 | 5F05 | 64 | 0563 | 0163 | 356 | All | 1
C01 | Jump Frequency 1 | ✔ | ✔ | C | 01 | 5F06 | 02 | 0601 | 0201 | 514 | All | 3
C02 | Jump Frequency 2 | ✔ | ✔ | C | 02 | 5F06 | 03 | 0602 | 0202 | 515 | All | 3
C03 | Jump Frequency 3 | ✔ | ✔ | C | 03 | 5F06 | 04 | 0603 | 0203 | 516 | All | 3
C04 | Jump Frequency (Hysteresis width) | ✔ | ✔ | C | 04 | 5F06 | 05 | 0604 | 0204 | 517 | All | 3
C05 | Multistep Frequency 1 | ✔ | ✔ | C | 05 | 5F06 | 06 | 0605 | 0205 | 518 | All | 22
C06 | Multistep Frequency 2 | ✔ | ✔ | C | 06 | 5F06 | 07 | 0606 | 0206 | 519 | All | 22
C07 | Multistep Frequency 3 | ✔ | ✔ | C | 07 | 5F06 | 08 | 0607 | 0207 | 520 | All | 22
C08 | Multistep Frequency 4 | ✔ | ✔ | C | 08 | 5F06 | 09 | 0608 | 0208 | 521 | All | 22
C09 | Multistep Frequency 5 | ✔ | ✔ | C | 09 | 5F06 | 0A | 0609 | 0209 | 522 | All | 22
C10 | Multistep Frequency 6 | ✔ | ✔ | C | 10 | 5F06 | 0B | 060A | 020A | 523 | All | 22
C11 | Multistep Frequency 7 | ✔ | ✔ | C | 11 | 5F06 | 0C | 060B | 020B | 524 | All | 22
C12 | Multistep Frequency 8 | ✔ | ✔ | C | 12 | 5F06 | 0D | 060C | 020C | 525 | All | 22
C13 | Multistep Frequency 9 | ✔ | ✔ | C | 13 | 5F06 | 0E | 060D | 020D | 526 | All | 22
C14 | Multistep Frequency 10 | ✔ | ✔ | C | 14 | 5F06 | 0F | 060E | 020E | 527 | All | 22
C15 | Multistep Frequency 11 | ✔ | ✔ | C | 15 | 5F06 | 10 | 060F | 020F | 528 | All | 22
C16 | Multistep Frequency 12 | ✔ | ✔ | C | 16 | 5F06 | 11 | 0610 | 0210 | 529 | All | 22
C17 | Multistep Frequency 13 | ✔ | ✔ | C | 17 | 5F06 | 12 | 0611 | 0211 | 530 | All | 22
C18 | Multistep Frequency 14 | ✔ | ✔ | C | 18 | 5F06 | 13 | 0612 | 0212 | 531 | All | 22
C19 | Multistep Frequency 15 | ✔ | ✔ | C | 19 | 5F06 | 14 | 0613 | 0213 | 532 | All | 22
C21 | Pattern Operation(Mode selection) | ✔ | ✔ | C | 21 | 5F06 | 16 | 0615 | 0215 | 534 | All | 1
C22 | Pattern Operation(Stage 1) | ✔ | ✔ | C | 22 | 5F06 | 17 | 0616 | 0216 | 535 | All | 84
C23 | Pattern Operation(Stage 2) | ✔ | ✔ | C | 23 | 5F06 | 18 | 0617 | 0217 | 536 | All | 84
C24 | Pattern Operation(Stage 3) | ✔ | ✔ | C | 24 | 5F06 | 19 | 0618 | 0218 | 537 | All | 84
C25 | Pattern Operation(Stage 4) | ✔ | ✔ | C | 25 | 5F06 | 1A | 0619 | 0219 | 538 | All | 84
C26 | Pattern Operation(Stage 5) | ✔ | ✔ | C | 26 | 5F06 | 1B | 061A | 021A | 539 | All | 84
C27 | Pattern Operation(Stage 6) | ✔ | ✔ | C | 27 | 5F06 | 1C | 061B | 021B | 540 | All | 84
C28 | Pattern Operation(Stage 7) | ✔ | ✔ | C | 28 | 5F06 | 1D | 061C | 021C | 541 | All | 84
C30 | Frequency Command 2 | ✔ | ✔ | C | 30 | 5F06 | 1F | 061E | 021E | 543 | All | 1
C31 | Analog Input Adjustment for [12] (offset) | ✔ | ✔ | C | 31 | 5F06 | 20 | 061F | 021F | 544 | All | 4
C32 | Analog Input Adjustment for [12] (Gain) | ✔ | ✔ | C | 32 | 5F06 | 21 | 0620 | 0220 | 545 | All | 5
C33 | Analog input Adjustment for [12] (Filter time constant) | ✔ | ✔ | C | 33 | 5F06 | 22 | 0621 | 0221 | 546 | All | 5
C34 | Analog input Adjustment for [12] (Gain base point) | ✔ | ✔ | C | 34 | 5F06 | 23 | 0622 | 0222 | 547 | All | 5
C35 | Analog input Adjustment for [12] (Polarity) | ✔ | ✔ | C | 35 | 5F06 | 24 | 0623 | 0223 | 548 | All | 1
C36 | Analog Input Adjustment for [C1] (offset) | ✔ | ✔ | C | 36 | 5F06 | 25 | 0624 | 0224 | 549 | All | 4
C37 | Analog Input Adjustment for [C1] (Gain) | ✔ | ✔ | C | 37 | 5F06 | 26 | 0625 | 0225 | 550 | All | 5
C38 | Analog input Adjustment for [C1] (Filter time constant) | ✔ | ✔ | C | 38 | 5F06 | 27 | 0626 | 0226 | 551 | All | 5
C39 | Analog input Adjustment for [C1] (Gain base point) | ✔ | ✔ | C | 39 | 5F06 | 28 | 0627 | 0227 | 552 | All | 5
C40 | Terminal [C1] Input Range Selection | ✔ | ✔ | C | 40 | 5F06 | 29 | 0628 | 0228 | 553 | All | 1
C41 | Analog Input Adjustment for [V2] (offset) | ✔ | ✔ | C | 41 | 5F06 | 2A | 0629 | 0229 | 554 | All | 4
C42 | Analog Input Adjustment for [V2] (Gain) | ✔ | ✔ | C | 42 | 5F06 | 2B | 062A | 022A | 555 | All | 5
C43 | Analog input Adjustment for [V2] (Filter time constant) | ✔ | ✔ | C | 43 | 5F06 | 2C | 062B | 022B | 556 | All | 5
C44 | Analog input Adjustment for [V2] (Gain base point) | ✔ | ✔ | C | 44 | 5F06 | 2D | 062C | 022C | 557 | All | 5
C45 | Analog input Adjustment for [V2] (Polarity) | ✔ | ✔ | C | 45 | 5F06 | 2E | 062D | 022D | 558 | All | 1
C50 | Bias Point (Frequency command 1) | ✔ | ✔ | C | 50 | 5F06 | 33 | 0632 | 0232 | 563 | All | 5
C53 | Selection of Normal/Inverse Operation (Frequency command 1) | ✔ | ✔ | C | 53 | 5F06 | 36 | 0635 | 0235 | 566 | All | 1
C55 | Analog Input Adjustment for Terminal[12](Bias value) | ✔ | ✔ | C | 55 | 5F06 | 38 | 0637 | 0237 | 568 | All | 6
C56 | Analog Input Adjustment for Terminal[12](Bias base point) | ✔ | ✔ | C | 56 | 5F06 | 39 | 0638 | 0238 | 569 | All | 5
C58 | Analog Input Adjustment for Terminal[12](Display unit) | ✔ | ✔ | C | 58 | 5F06 | 3B | 063A | 023A | 571 | All | 1
C59 | Analog Input Adjustment for Terminal[12](Maximum scale) | ✔ | ✔ | C | 59 | 5F06 | 3C | 063B | 023B | 572 | All | 12
C60 | Analog Input Adjustment for Terminal[12](Minimum scale) | ✔ | ✔ | C | 60 | 5F06 | 3D | 063C | 023C | 573 | All | 12
C61 | Analog Input Adjustment for Terminal[C1](Bias value) | ✔ | ✔ | C | 61 | 5F06 | 3E | 063D | 023D | 574 | All | 6
C62 | Analog Input Adjustment for Terminal[C1](Bias base point) | ✔ | ✔ | C | 62 | 5F06 | 3F | 063E | 023E | 575 | All | 5
C64 | Analog Input Adjustment for Terminal[C1](Display unit) | ✔ | ✔ | C | 64 | 5F06 | 41 | 0640 | 0240 | 577 | All | 1
C65 | Analog Input Adjustment for Terminal[C1](Maximum scale) | ✔ | ✔ | C | 65 | 5F06 | 42 | 0641 | 0241 | 578 | All | 12
C66 | Analog Input Adjustment for Terminal[C1](minimum scale) | ✔ | ✔ | C | 66 | 5F06 | 43 | 0642 | 0242 | 579 | All | 12
C67 | Analog Input Adjustment for Terminal[V2](Bias value) | ✔ | ✔ | C | 67 | 5F06 | 44 | 0643 | 0243 | 580 | All | 6
C68 | Analog Input Adjustment for Terminal[V2](Bias base point) | ✔ | ✔ | C | 68 | 5F06 | 45 | 0644 | 0244 | 581 | All | 5
C70 | Analog Input Adjustment for Terminal[V2](Display unit) | ✔ | ✔ | C | 70 | 5F06 | 47 | 0646 | 0246 | 583 | All | 1
C71 | Analog Input Adjustment for Terminal[V2](Maximum scale) | ✔ | ✔ | C | 71 | 5F06 | 48 | 0647 | 0247 | 584 | All | 12
C72 | Analog Input Adjustment for Terminal[V2](Miniimum scale) | ✔ | ✔ | C | 72 | 5F06 | 49 | 0648 | 0248 | 585 | All | 12
C94 | Jump Frequency 4 | ✔ | ✔ | C | 94 | 5F06 | 5F | 065E | 025E | 607 | All | 3
C95 | Jump Frequency 5 | ✔ | ✔ | C | 95 | 5F06 | 60 | 065F | 025F | 608 | All | 3
C96 | Jump Frequency 6 | ✔ | ✔ | C | 96 | 5F06 | 61 | 0660 | 0260 | 609 | All | 3
P01 | Motor 1 (No. of poles) | ✔ | ✔ | P | 01 | 5F07 | 02 | 0701 | 0301 | 770 | All | 1
P02 | Motor 1 (Rated capacity) | ✔ | ✔ | P | 02 | 5F07 | 03 | 0702 | 0302 | 771 | All | 11
P03 | Motor 1 (Rated current) | ✔ | ✔ | P | 03 | 5F07 | 04 | 0703 | 0303 | 772 | FGI | 24
P03 | Motor 1 (Rated current) | ✔ | ✔ | P | 03 | 5F07 | 04 | 0703 | 0303 | 772 | RTU | 19
P03 | Motor 1 (Rated current) | ✔ | ✔ | P | 03 | 5F07 | 04 | 0703 | 0303 | 772 | BUS | 24
P04 | Motor 1 (Auto Tuning) | ✔ | ✔ | P | 04 | 5F07 | 05 | 0704 | 0304 | 773 | All | 21
P05 | Motor 1 (Online-Tuning) | ✔ | ✔ | P | 05 | 5F07 | 06 | 0705 | 0305 | 774 | All | 1
P06 | Motor 1 (No-load current) | ✔ | ✔ | P | 06 | 5F07 | 07 | 0706 | 0306 | 775 | FGI | 24
P06 | Motor 1 (No-load current) | ✔ | ✔ | P | 06 | 5F07 | 07 | 0706 | 0306 | 775 | RTU | 19
P06 | Motor 1 (No-load current) | ✔ | ✔ | P | 06 | 5F07 | 07 | 0706 | 0306 | 775 | BUS | 24
P07 | Motor 1 (%R1) | ✔ | ✔ | P | 07 | 5F07 | 08 | 0707 | 0307 | 776 | All | 5
P08 | Motor 1 (%X) | ✔ | ✔ | P | 08 | 5F07 | 09 | 0708 | 0308 | 777 | All | 5
P10 | Motor 1 (Slip compensation response time) | ✔ | ✔ | P | 10 | 5F07 | 0B | 070A | 030A | 779 | All | 5
P12 | Motor 1 (Rated slip frequency) | ✔ | ✔ | P | 12 | 5F07 | 0D | 070C | 030C | 781 | All | 5
P99 | Motor 1 Selection | ✔ | ✔ | P | 99 | 5F07 | 64 | 0763 | 0363 | 868 | All | 1
H03 | Data Initialization | ✔ | ✔ | H | 03 | 5F08 | 04 | 0803 | 0403 | 1028 | All | 1
H04 | Auto-reset (Times) | ✔ | ✔ | H | 04 | 5F08 | 05 | 0804 | 0404 | 1029 | All | 1
H05 | Auto-reset (Reset interval) | ✔ | ✔ | H | 05 | 5F08 | 06 | 0805 | 0405 | 1030 | All | 3
H06 | Cooling Fan ON/OFF Control | ✔ | ✔ | H | 06 | 5F08 | 07 | 0806 | 0406 | 1031 | All | 1
H07 | Acceleration/Deceleration Pattern | ✔ | ✔ | H | 07 | 5F08 | 08 | 0807 | 0407 | 1032 | All | 1
H08 | Rotational Direction Limitation | ✔ | ✔ | H | 08 | 5F08 | 09 | 0808 | 0408 | 1033 | All | 1
H09 | Starting Mode (Auto search) | ✔ | ✔ | H | 09 | 5F08 | 0A | 0809 | 0409 | 1034 | All | 1
H11 | Deceleration Mode | ✔ | ✔ | H | 11 | 5F08 | 0C | 080B | 040B | 1036 | All | 1
H12 | Instantaneous Overcurrent Limiting (Mode selection) | ✔ | ✔ | H | 12 | 5F08 | 0D | 080C | 040C | 1037 | All | 1
H13 | Restart Mode after Momentary Power Failure (Restart time) | ✔ | ✔ | H | 13 | 5F08 | 0E | 080D | 040D | 1038 | All | 3
H14 | Restart Mode after Momentary Power Failure (Frequency fall rate) | ✔ | ✔ | H | 14 | 5F08 | 0F | 080E | 040E | 1039 | All | 5
H15 | Restart Mode after Momentary Power Failure (Continuous running level) | ✔ | ✔ | H | 15 | 5F08 | 10 | 080F | 040F | 1040 | All | 1
H16 | Restart Mode after Momentary Power Failure (Allowable time) | ✔ | ✔ | H | 16 | 5F08 | 11 | 0810 | 0410 | 1041 | All | 3
H26 | Thermistor (for motor) (Mode selection) | ✔ | ✔ | H | 26 | 5F08 | 1B | 081A | 041A | 1051 | All | 1
H27 | Thermistor (for motor) (Level) | ✔ | ✔ | H | 27 | 5F08 | 1C | 081B | 041B | 1052 | All | 5
H30 | Communications Link Function (Mode selection) | ✔ | ✔ | H | 30 | 5F08 | 1F | 081E | 041E | 1055 | All | 1
H42 | Capacitance of DC Link Bus Capacitor | ✔ | ✔ | H | 42 | 5F08 | 2B | 082A | 042A | 1067 | All | 1
H43 | Cumulative Run Time of Cooling Fan | ✔ | ✔ | H | 43 | 5F08 | 2C | 082B | 042B | 1068 | All | 74
H44 | Startup Counter for Motor 1 | ✔ | ✔ | H | 44 | 5F08 | 2D | 082C | 042C | 1069 | All | 1
H45 | Mock Alarm | ✔ | ✔ | H | 45 | 5F08 | 2E | 082D | 042D | 1070 | All | 1
H46 | Starting Mode (Auto search delay time 2) | ✔ | ✔ | H | 46 | 5F08 | 2F | 082E | 042E | 1071 | All | 3
H47 | Initial Capacitance of DC Link Bus Capacitor | ✔ | ✔ | H | 47 | 5F08 | 30 | 082F | 042F | 1072 | All | 1
H48 | Cumulative Run Time of Capacitors on Printed Circuit Boards | ✔ | ✔ | H | 48 | 5F08 | 31 | 0830 | 0430 | 1073 | All | 74
H49 | Starting Mode (Auto search delay time 1) | ✔ | ✔ | H | 49 | 5F08 | 32 | 0831 | 0431 | 1074 | All | 3
H50 | Non-linear V/f Pattern 1 (Frequency) | ✔ | ✔ | H | 50 | 5F08 | 33 | 0832 | 0432 | 1075 | All | 3
H51 | Non-linear V/f Pattern 1 (Voltage) | ✔ | ✔ | H | 51 | 5F08 | 34 | 0833 | 0433 | 1076 | All | 1
H52 | Non-linear V/f Pattern 2 (Frequency) | ✔ | ✔ | H | 52 | 5F08 | 35 | 0834 | 0434 | 1077 | All | 3
H53 | Non-linear V/f Pattern 2 (Voltage) | ✔ | ✔ | H | 53 | 5F08 | 36 | 0835 | 0435 | 1078 | All | 1
H56 | Deceleration Time for Forced Stop | ✔ | ✔ | H | 56 | 5F08 | 39 | 0838 | 0438 | 1081 | All | 12
H61 | UP/DOWN Control (Initial frequency setting) | ✔ | ✔ | H | 61 | 5F08 | 3E | 083D | 043D | 1086 | All | 1
H63 | Low Limiter (Mode selection) | ✔ | ✔ | H | 63 | 5F08 | 40 | 083F | 043F | 1088 | All | 1
H64 | Low Limiter (Lower limiting frequency) | ✔ | ✔ | H | 64 | 5F08 | 41 | 0840 | 0440 | 1089 | All | 3
H68 | Slip Compensation 1 (Operating conditions) | ✔ | ✔ | H | 68 | 5F08 | 45 | 0844 | 0444 | 1093 | All | 1
H69 | Automatic Deceleration (Mode selection) | ✔ | ✔ | H | 69 | 5F08 | 46 | 0845 | 0445 | 1094 | All | 1
H70 | Overload Prevention control | ✔ | ✔ | H | 70 | 5F08 | 47 | 0846 | 0446 | 1095 | All | 5
H71 | Deceleration Characteristics | ✔ | ✔ | H | 71 | 5F08 | 48 | 0847 | 0447 | 1096 | All | 1
H72 | Main Power Down Detection (Mode selection) | ✔ | ✔ | H | 72 | 5F08 | 49 | 0848 | 0448 | 1097 | All | 1
H76 | Torque Limiter for Braking(Frequency increment limit) | ✔ | ✔ | H | 76 | 5F08 | 4D | 084C | 044C | 1101 | All | 3
H77 | Service Life of DC Link Bus Capacitor (Remaining time) | ✔ | ✔ | H | 77 | 5F08 | 4E | 084D | 044D | 1102 | All | 74
H78 | Maintenance Interval (M1) | ✔ | ✔ | H | 78 | 5F08 | 4F | 084E | 044E | 1103 | All | 74
H79 | Preset Startup Count for Maintenance (M1) | ✔ | ✔ | H | 79 | 5F08 | 50 | 084F | 044F | 1104 | All | 1
H80 | Output Current Fluctuation Damping Gain for Motor 1 | ✔ | ✔ | H | 80 | 5F08 | 51 | 0850 | 0450 | 1105 | All | 5
H89 | Reserved | ✔ | ✔ | H | 89 | 5F08 | 5A | 0859 | 0459 | 1114 | All | 1
H90 | Reserved | ✔ | ✔ | H | 90 | 5F08 | 5B | 085A | 045A | 1115 | All | 1
H91 | Current Input Wire Break Detection | ✔ | ✔ | H | 91 | 5F08 | 5C | 085B | 045B | 1116 | All | 3
H92 | Continuity of Running (P) | ✔ | ✔ | H | 92 | 5F08 | 5D | 085C | 045C | 1117 | All | 7
H93 | Continuity of Running (I) | ✔ | ✔ | H | 93 | 5F08 | 5E | 085D | 045D | 1118 | All | 7
H94 | Cumulative Motor Run Time 1 | ✔ | ✔ | H | 94 | 5F08 | 5F | 085E | 045E | 1119 | All | 74
H95 | DC Braking (Braking response mode) | ✔ | ✔ | H | 95 | 5F08 | 60 | 085F | 045F | 1120 | All | 1
H96 | STOP Key Priority / Start Check Function | ✔ | ✔ | H | 96 | 5F08 | 61 | 0860 | 0460 | 1121 | All | 1
H97 | Clear Alarm Data | ✔ | ✔ | H | 97 | 5F08 | 62 | 0861 | 0461 | 1122 | All | 1
H98 | Protection / Maintenance Function (Mode selection) | ✔ | ✔ | H | 98 | 5F08 | 63 | 0862 | 0462 | 1123 | All | 1
H104 | Number-of-retry Clear Time | ✔ | ✔ | H1 | 04 | 5F20 | 05 | 2004 | 1F04 | 7941 | All | 3
H105 | Retry Target Selection | ✔ | ✔ | H1 | 05 | 5F20 | 06 | 2005 | 1F05 | 7942 | All | 1
H106 | Retry Target Selection2 | ✔ | ✔ | H1 | 06 | 5F20 | 07 | 2006 | 1F06 | 7943 | All | 1
H110 | Input Phase Lose Protection Avoidance Operation(Mode selection) | ✔ | ✔ | H1 | 10 | 5F20 | 0B | 200A | 1F0A | 7947 | All | 1
H112 | Voltage Shortage Avoidance Operation(Mode selection) | ✔ | ✔ | H1 | 12 | 5F20 | 0D | 200C | 1F0C | 7949 | All | 1
H114 | Automatic Deceleration (Operation level) | ✔ | ✔ | H1 | 14 | 5F20 | 0F | 200E | 1F0E | 7951 | All | 3
H116 | Fire Mode(Mode selection) | ✔ | ✔ | H1 | 16 | 5F20 | 11 | 2010 | 1F10 | 7953 | All | 1
H117 | Fire Mode(Confirmation time) | ✔ | ✔ | H1 | 17 | 5F20 | 12 | 2011 | 1F11 | 7954 | All | 3
H118 | Fire Mode(Reference frequency) | ✔ | ✔ | H1 | 18 | 5F20 | 13 | 2012 | 1F12 | 7955 | All | 3
H119 | Fire Mode(Run command) | ✔ | ✔ | H1 | 19 | 5F20 | 14 | 2013 | 1F13 | 7956 | All | 1
H120 | Fire Mode(Start method) | ✔ | ✔ | H1 | 20 | 5F20 | 15 | 2014 | 1F14 | 7957 | All | 1
H121 | Fire Mode(Reset interval) | ✔ | ✔ | H1 | 21 | 5F20 | 16 | 2015 | 1F15 | 7958 | All | 3
H122 | Cooling Fan Minimum Operating Time | ✔ | ✔ | H1 | 22 | 5F20 | 17 | 2016 | 1F16 | 7959 | All | 74
H181 | Light Alarm Selection 1 | ✔ | ✔ | H1 | 81 | 5F20 | 52 | 2051 | 1F51 | 8018 | All | 1
H182 | Light Alarm Selection 2 | ✔ | ✔ | H1 | 82 | 5F20 | 53 | 2052 | 1F52 | 8019 | All | 1
H183 | Light Alarm Selection 3 | ✔ | ✔ | H1 | 83 | 5F20 | 54 | 2053 | 1F53 | 8020 | All | 1
H184 | Light Alarm Selection 4 | ✔ | ✔ | H1 | 84 | 5F20 | 55 | 2054 | 1F54 | 8021 | All | 1
H197 | User Password1(Mode selection) | ✔ | ✔ | H1 | 97 | 5F20 | 62 | 2061 | 1F61 | 8034 | All | 1
J21 | Dew Condensation Prevention (Duty) | ✔ | ✔ | J | 21 | 5F0E | 16 | 0E15 | 0D15 | 3350 | All | 1
J22 | Commercial Power Switching Sequence | ✔ | ✔ | J | 22 | 5F0E | 17 | 0E16 | 0D16 | 3351 | All | 1
J101 | PID Control1 (Mode selection) | ✔ | ✔ | J1 | 01 | 5F24 | 02 | 2401 | 3001 | 12290 | All | 1
J102 | PID Control1 (Command selection) | ✔ | ✔ | J1 | 02 | 5F24 | 03 | 2402 | 3002 | 12291 | All | 1
J103 | PID Control1 (Feedback selection) | ✔ | ✔ | J1 | 03 | 5F24 | 04 | 2403 | 3003 | 12292 | All | 1
J104 | PID Control1 (Deviation selection) | ✔ | ✔ | J1 | 04 | 5F24 | 05 | 2404 | 3004 | 12293 | All | 1
J105 | PID Control1 (Display unit) | ✔ | ✔ | J1 | 05 | 5F24 | 06 | 2405 | 3005 | 12294 | All | 1
J106 | PID Control1 (Maximum scale) | ✔ | ✔ | J1 | 06 | 5F24 | 07 | 2406 | 3006 | 12295 | All | 12
J107 | PID Control1 (minimum scale) | ✔ | ✔ | J1 | 07 | 5F24 | 08 | 2407 | 3007 | 12296 | All | 12
J108 | PID Control1 (Auto tuning) | ✔ | ✔ | J1 | 08 | 5F24 | 09 | 2408 | 3008 | 12297 | All | 1
J109 | PID Control1 (Tuninng MV) | ✔ | ✔ | J1 | 09 | 5F24 | 0A | 2409 | 3009 | 12298 | All | 1
J110 | PID Control1 P (gain) | ✔ | ✔ | J1 | 10 | 5F24 | 0B | 240A | 300A | 12299 | All | 7
J111 | PID Control1 I (Integral time) | ✔ | ✔ | J1 | 11 | 5F24 | 0C | 240B | 300B | 12300 | All | 3
J112 | PID Control1 D (Differential time) | ✔ | ✔ | J1 | 12 | 5F24 | 0D | 240C | 300C | 12301 | All | 5
J113 | PID Control1 (Feedback filter) | ✔ | ✔ | J1 | 13 | 5F24 | 0E | 240D | 300D | 12302 | All | 3
J114 | PID Control1 (Anti-reset wind-up) | ✔ | ✔ | J1 | 14 | 5F24 | 0F | 240E | 300E | 12303 | All | 12
J118 | PID Control1 (Upper limit of PID process output) | ✔ | ✔ | J1 | 18 | 5F24 | 13 | 2412 | 3012 | 12307 | All | 3
J119 | PID Control1 (Lower limit of PID process output) | ✔ | ✔ | J1 | 19 | 5F24 | 14 | 2413 | 3013 | 12308 | All | 3
J121 | PID Control1 (Alarm output selection) | ✔ | ✔ | J1 | 21 | 5F24 | 16 | 2415 | 3015 | 12310 | All | 1
J122 | PID Control1 (Upper level alarm (AH)) | ✔ | ✔ | J1 | 22 | 5F24 | 17 | 2416 | 3016 | 12311 | All | 12
J124 | PID Control1 (Lower level alarm (AL)) | ✔ | ✔ | J1 | 24 | 5F24 | 19 | 2418 | 3018 | 12313 | All | 12
J127 | PID Control1 (Feedback failure detection(Mode selection)) | ✔ | ✔ | J1 | 27 | 5F24 | 1C | 241B | 301B | 12316 | All | 1
J128 | PID Control1 (Feedback failure continuation durationj | ✔ | ✔ | J1 | 28 | 5F24 | 1D | 241C | 301C | 12317 | All | 1
J129 | PID Control1(Feedback failure upper-limit) | ✔ | ✔ | J1 | 29 | 5F24 | 1E | 241D | 301D | 12318 | All | 12
J130 | PID Control1 (Feedback failure lower-limit) | ✔ | ✔ | J1 | 30 | 5F24 | 1F | 241E | 301E | 12319 | All | 12
J131 | PID Control1 (Feedback failure detection time) | ✔ | ✔ | J1 | 31 | 5F24 | 20 | 241F | 301F | 12320 | All | 3
J136 | PID Multistep Command (Multistep command1) | ✔ | ✔ | J1 | 36 | 5F24 | 25 | 2424 | 3024 | 12325 | All | 12
J137 | PID Multistep Command (Multistep command2) | ✔ | ✔ | J1 | 37 | 5F24 | 26 | 2425 | 3025 | 12326 | All | 12
J138 | PID Multistep Command (Multistep command3) | ✔ | ✔ | J1 | 38 | 5F24 | 27 | 2426 | 3026 | 12327 | All | 12
J143 | Boost Function (Mode selection) | ✔ | x | J1 | 43 | 5F24 | 2C | 242B | 302B | 12332 | All | 1
J144 | Boost Function (Operation frequncy) | ✔ | x | J1 | 44 | 5F24 | 2D | 242C | 302C | 12333 | All | 3
J145 | Boost Function (Acceleration time) | ✔ | x | J1 | 45 | 5F24 | 2E | 242D | 302D | 12334 | All | 12
J146 | Boost Function (Operation time) | ✔ | x | J1 | 46 | 5F24 | 2F | 242E | 302E | 12335 | All | 3
J147 | Boost Function (Cancel PV level) | ✔ | x | J1 | 47 | 5F24 | 30 | 242F | 302F | 12336 | All | 12
J149 | Slow Flowrate Stop Function (Mode selection) | ✔ | x | J1 | 49 | 5F24 | 32 | 2431 | 3031 | 12338 | All | 1
J150 | Slow Flowrate Stop Function (Operation level) | ✔ | x | J1 | 50 | 5F24 | 33 | 2432 | 3032 | 12339 | All | 12
J151 | Slow Flowrate Stop Function (Elapsed time) | ✔ | x | J1 | 51 | 5F24 | 34 | 2433 | 3033 | 12340 | All | 1
J152 | Slow Flowrate Stop Function(Auto-operation frequency lower-limit) | ✔ | x | J1 | 52 | 5F24 | 35 | 2434 | 3034 | 12341 | All | 3
J153 | Slow Flowrate Stop Function (Pressurization starting frequency) | ✔ | x | J1 | 53 | 5F24 | 36 | 2435 | 3035 | 12342 | All | 3
J154 | Slow Flowrate Stop Function (Pressurizing time) | ✔ | x | J1 | 54 | 5F24 | 37 | 2436 | 3036 | 12343 | All | 1
J156 | Slow Flowrate Stop Function (Initiation inhibition time) | ✔ | x | J1 | 56 | 5F24 | 39 | 2438 | 3038 | 12345 | All | 1
J157 | Slow Flowrate Stop Function (Cancel frequency) | ✔ | x | J1 | 57 | 5F24 | 3A | 2439 | 3039 | 12346 | All | 3
J158 | Slow Flowrate Stop Function (Cancel deviation level1) | ✔ | x | J1 | 58 | 5F24 | 3B | 243A | 303A | 12347 | All | 12
J159 | Slow Flowrate Stop Function (Cancel delay timer) | ✔ | x | J1 | 59 | 5F24 | 3C | 243B | 303B | 12348 | All | 1
J160 | Slow Flowrate Stop Function (Cancel deviation level2) | ✔ | x | J1 | 60 | 5F24 | 3D | 243C | 303C | 12349 | All | 12
J163 | Flow Sensor (Input selection) | ✔ | x | J1 | 63 | 5F24 | 40 | 243F | 303F | 12352 | All | 1
J164 | Flow Sensor (ON level) | ✔ | x | J1 | 64 | 5F24 | 41 | 2440 | 3040 | 12353 | All | 12
J165 | Flow Sensor (OFF level) | ✔ | x | J1 | 65 | 5F24 | 42 | 2441 | 3041 | 12354 | All | 12
J166 | Flow Sensor (Input filter) | ✔ | x | J1 | 66 | 5F24 | 43 | 2442 | 3042 | 12355 | All | 5
J168 | Control of Maximum Starts Per Hour (Input selection) | ✔ | x | J1 | 68 | 5F24 | 45 | 2444 | 3044 | 12357 | All | 1
J169 | Control of Maximum Starts Per Hour (Number of detections) | ✔ | x | J1 | 69 | 5F24 | 46 | 2445 | 3045 | 12358 | All | 1
J176 | Dry Pump Protection (Input selection) | ✔ | x | J1 | 76 | 5F24 | 4D | 244C | 304C | 12365 | All | 1
J177 | Dry Pump Protection (Detection current) | ✔ | x | J1 | 77 | 5F24 | 4E | 244D | 304D | 12366 | All | 24
J178 | Dry Pump Protection (Deviation) | ✔ | x | J1 | 78 | 5F24 | 4F | 244E | 304E | 12367 | All | 12
J179 | Dry Pump Protection (Flow sensor) | ✔ | x | J1 | 79 | 5F24 | 50 | 244F | 304F | 12368 | All | 1
J180 | Dry Pump Protection (Detection timer) | ✔ | x | J1 | 80 | 5F24 | 51 | 2450 | 3050 | 12369 | All | 1
J182 | End of Protection (Input selection) | ✔ | x | J1 | 82 | 5F24 | 53 | 2452 | 3052 | 12371 | All | 1
J183 | End of Protection (Detection current) | ✔ | x | J1 | 83 | 5F24 | 54 | 2453 | 3053 | 12372 | All | 24
J184 | End of Protection (Deviation) | ✔ | x | J1 | 84 | 5F24 | 55 | 2454 | 3054 | 12373 | All | 12
J185 | End of Protection (Flow sensor) | ✔ | x | J1 | 85 | 5F24 | 56 | 2455 | 3055 | 12374 | All | 1
J186 | End of Protection (Detection timer) | ✔ | x | J1 | 86 | 5F24 | 57 | 2456 | 3056 | 12375 | All | 1
J188 | Filter Clogging Prevention/Anti Jam Func. (Input selection) | ✔ | ✔ | J1 | 88 | 5F24 | 59 | 2458 | 3058 | 12377 | All | 1
J189 | Filter Clogging Prevention (Reverse operation cycle time) | ✔ | ✔ | J1 | 89 | 5F24 | 5A | 2459 | 3059 | 12378 | All | 1
J190 | Filter Clogging Prevention (Load resistance current) | ✔ | ✔ | J1 | 90 | 5F24 | 5B | 245A | 305A | 12379 | All | 24
J191 | Filter Clogging Prevention (Load resistance PV signal) | ✔ | ✔ | J1 | 91 | 5F24 | 5C | 245B | 305B | 12380 | All | 12
J192 | Filter Clogging Prevention (Load resistance detection timer) | ✔ | ✔ | J1 | 92 | 5F24 | 5D | 245C | 305C | 12381 | All | 1
J193 | Filter Clogging Prevention/Anti Jam Func. (Reverse operation frequency) | ✔ | ✔ | J1 | 93 | 5F24 | 5E | 245D | 305D | 12382 | All | 3
J194 | Filter Clogging Prevention/Anti Jam Func. (Reverse operation time) | ✔ | ✔ | J1 | 94 | 5F24 | 5F | 245E | 305E | 12383 | All | 1
J195 | Filter Clogging Prevention/Anti Jam Func. (Number of reverse runs) | ✔ | ✔ | J1 | 95 | 5F24 | 60 | 245F | 305F | 12384 | All | 1
J198 | Wet-bulb temperature presumption control | x | ✔ | J1 | 98 | 5F24 | 63 | 2462 | 3062 | 12387 | All | 5
J201 | PID Control 2 (Mode selection) | ✔ | ✔ | J2 | 01 | 5F25 | 02 | 2501 | 3101 | 12546 | All | 1
J202 | PID Control 2 (Command selection) | ✔ | ✔ | J2 | 02 | 5F25 | 03 | 2502 | 3102 | 12547 | All | 1
J203 | PID Control 2 (Feedback selection) | ✔ | ✔ | J2 | 03 | 5F25 | 04 | 2503 | 3103 | 12548 | All | 1
J205 | PID Control 2 (Display unit) | ✔ | ✔ | J2 | 05 | 5F25 | 06 | 2505 | 3105 | 12550 | All | 1
J206 | PID Control 2 (Maximum scale) | ✔ | ✔ | J2 | 06 | 5F25 | 07 | 2506 | 3106 | 12551 | All | 12
J207 | PID Control 2 (Minimum scale) | ✔ | ✔ | J2 | 07 | 5F25 | 08 | 2507 | 3107 | 12552 | All | 12
J208 | PID Control 2 (Auto tuning) | ✔ | ✔ | J2 | 08 | 5F25 | 09 | 2508 | 3108 | 12553 | All | 1
J209 | PID Control 2 (Tuninng MV) | ✔ | ✔ | J2 | 09 | 5F25 | 0A | 2509 | 3109 | 12554 | All | 1
J210 | PID Control 2 P (Gain) | ✔ | ✔ | J2 | 10 | 5F25 | 0B | 250A | 310A | 12555 | All | 7
J211 | PID Control 2 I (Integral time) | ✔ | ✔ | J2 | 11 | 5F25 | 0C | 250B | 310B | 12556 | All | 3
J212 | PID Control 2 D (Differential time) | ✔ | ✔ | J2 | 12 | 5F25 | 0D | 250C | 310C | 12557 | All | 5
J213 | PID Control 2 (Feedback filter) | ✔ | ✔ | J2 | 13 | 5F25 | 0E | 250D | 310D | 12558 | All | 3
J214 | PID Control 2 (Anti-reset wind-up) | ✔ | ✔ | J2 | 14 | 5F25 | 0F | 250E | 310E | 12559 | All | 12
J218 | PID Control 2 (Upper limit of PID process output) | ✔ | ✔ | J2 | 18 | 5F25 | 13 | 2512 | 3112 | 12563 | All | 3
J219 | PID Control 2 (Lower limit of PID process output) | ✔ | ✔ | J2 | 19 | 5F25 | 14 | 2513 | 3113 | 12564 | All | 3
J221 | PID Control 2 PID Control 2 (Alarm output selection) | ✔ | ✔ | J2 | 21 | 5F25 | 16 | 2515 | 3115 | 12566 | All | 1
J222 | PID Control 2 (Upper level alarm (AH)) | ✔ | ✔ | J2 | 22 | 5F25 | 17 | 2516 | 3116 | 12567 | All | 12
J223 | PID Control 2 (Upper level alarm detection hysteresis width) | ✔ | ✔ | J2 | 23 | 5F25 | 18 | 2517 | 3117 | 12568 | All | 12
J224 | PID Control 2 (Lower level alarm (AL)) | ✔ | ✔ | J2 | 24 | 5F25 | 19 | 2518 | 3118 | 12569 | All | 12
J225 | PID Control 2 (Upper level alarm detection hysteresis width) | ✔ | ✔ | J2 | 25 | 5F25 | 1A | 2519 | 3119 | 12570 | All | 12
J227 | PID Control 2 (Feedback failure detection (Mode selection)) | ✔ | ✔ | J2 | 27 | 5F25 | 1C | 251B | 311B | 12572 | All | 1
J228 | PID Control 2 (Feedback failure continuation duration) | ✔ | ✔ | J2 | 28 | 5F25 | 1D | 251C | 311C | 12573 | All | 1
J229 | PID Control 2 (Feedback failure upper-limit) | ✔ | ✔ | J2 | 29 | 5F25 | 1E | 251D | 311D | 12574 | All | 12
J230 | PID Control 2 (Feedback failure lower-limit) | ✔ | ✔ | J2 | 30 | 5F25 | 1F | 251E | 311E | 12575 | All | 12
J231 | PID Control 2 (Feedback failure detection time) | ✔ | ✔ | J2 | 31 | 5F25 | 20 | 251F | 311F | 12576 | All | 3
J247 | Boost Function (Cancel PV level) | ✔ | x | J2 | 47 | 5F25 | 30 | 252F | 312F | 12592 | All | 12
J249 | Slow Flowrate Stop Function (Mode selection) | ✔ | x | J2 | 49 | 5F25 | 32 | 2531 | 3131 | 12594 | All | 1
J250 | Slow Flowrate Stop Function (Operation level) | ✔ | x | J2 | 50 | 5F25 | 33 | 2532 | 3132 | 12595 | All | 12
J251 | Slow Flowrate Stop Function (Elapsed time) | ✔ | x | J2 | 51 | 5F25 | 34 | 2533 | 3133 | 12596 | All | 1
J256 | Slow Flowrate Stop Function (Initiation inhibition time) | ✔ | x | J2 | 56 | 5F25 | 39 | 2538 | 3138 | 12601 | All | 1
J257 | Slow Flowrate Stop Function (Cancel frequency) | ✔ | x | J2 | 57 | 5F25 | 3A | 2539 | 3139 | 12602 | All | 3
J258 | Slow Flowrate Stop Function (Cancel deviation level 1) | ✔ | x | J2 | 58 | 5F25 | 3B | 253A | 313A | 12603 | All | 12
J259 | Slow Flowrate Stop Function (Cancel delay timer) | ✔ | x | J2 | 59 | 5F25 | 3C | 253B | 313B | 12604 | All | 1
J260 | Slow Flowrate Stop Function (Cancel deviation level 2) | ✔ | x | J2 | 60 | 5F25 | 3D | 253C | 313C | 12605 | All | 12
J276 | Dry Pump Protection (Input selection) | ✔ | x | J2 | 76 | 5F25 | 4D | 254C | 314C | 12621 | All | 1
J277 | Dry Pump Protection (Detection current) | ✔ | x | J2 | 77 | 5F25 | 4E | 254D | 314D | 12622 | All | 24
J278 | Dry Pump Protection (Deviation) | ✔ | x | J2 | 78 | 5F25 | 4F | 254E | 314E | 12623 | All | 12
J279 | Dry Pump Protection (Flow sensor) | ✔ | x | J2 | 79 | 5F25 | 50 | 254F | 314F | 12624 | All | 1
J280 | Dry Pump Protection (Detection timer) | ✔ | x | J2 | 80 | 5F25 | 51 | 2550 | 3150 | 12625 | All | 1
J401 | Pump Control Mode Selection | ✔ | x | J4 | 01 | 5F27 | 02 | 2701 | 3301 | 13058 | All | 1
J402 | Communication Master/Slave Selection | ✔ | x | J4 | 02 | 5F27 | 03 | 2702 | 3302 | 13059 | All | 1
J403 | Number of Slaves | ✔ | x | J4 | 03 | 5F27 | 04 | 2703 | 3303 | 13060 | All | 1
J404 | Master Input Permeation Selection | ✔ | x | J4 | 04 | 5F27 | 05 | 2704 | 3304 | 13061 | All | 1
J411 | Motor 1 Mode Selection | ✔ | x | J4 | 11 | 5F27 | 0C | 270B | 330B | 13068 | All | 1
J412 | Motor 2 Mode Selection | ✔ | x | J4 | 12 | 5F27 | 0D | 270C | 330C | 13069 | All | 1
J413 | Motor 3 Mode Selection | ✔ | x | J4 | 13 | 5F27 | 0E | 270D | 330D | 13070 | All | 1
J414 | Motor 4 Mode Selection | ✔ | x | J4 | 14 | 5F27 | 0F | 270E | 330E | 13071 | All | 1
J415 | Motor 5 Mode Selection | ✔ | x | J4 | 15 | 5F27 | 10 | 270F | 330F | 13072 | All | 1
J416 | Motor 6 Mode Selection | ✔ | x | J4 | 16 | 5F27 | 11 | 2710 | 3310 | 13073 | All | 1
J417 | Motor 7 Mode Selection | ✔ | x | J4 | 17 | 5F27 | 12 | 2711 | 3311 | 13074 | All | 1
J418 | Motor 8 Mode Selection | ✔ | x | J4 | 18 | 5F27 | 13 | 2712 | 3312 | 13075 | All | 1
J425 | Motor Switching Procedure | ✔ | x | J4 | 25 | 5F27 | 1A | 2719 | 3319 | 13082 | All | 1
J430 | How to Stop the Motor | ✔ | x | J4 | 30 | 5F27 | 1F | 271E | 331E | 13087 | All | 1
J435 | Motor Regular Switching Mode Selection | ✔ | x | J4 | 35 | 5F27 | 24 | 2723 | 3323 | 13092 | All | 1
J436 | Motor Regular Switching Time | ✔ | x | J4 | 36 | 5F27 | 25 | 2724 | 3324 | 13093 | All | 3
J437 | Motor Regular Switching Signal Output Time | ✔ | x | J4 | 37 | 5F27 | 26 | 2725 | 3325 | 13094 | All | 5
J450 | Motor Increase Judgment (Judgment frequency) | ✔ | x | J4 | 50 | 5F27 | 33 | 2732 | 3332 | 13107 | All | 1
J451 | Motor Increase Judgment (Duration time) | ✔ | x | J4 | 51 | 5F27 | 34 | 2733 | 3333 | 13108 | All | 12
J452 | Motor Decrease Judgment (Judgment frequency) | ✔ | x | J4 | 52 | 5F27 | 35 | 2734 | 3334 | 13109 | All | 1
J453 | Motor Decrease Judgment (Duration time) | ✔ | x | J4 | 53 | 5F27 | 36 | 2735 | 3335 | 13110 | All | 12
J454 | Contactor Restart Time when Switching the Motor | ✔ | x | J4 | 54 | 5F27 | 37 | 2736 | 3336 | 13111 | All | 5
J455 | Motor Increase Switching Time (Deceleration time) | ✔ | x | J4 | 55 | 5F27 | 38 | 2737 | 3337 | 13112 | All | 12
J456 | Motor Increase Switching Level | ✔ | x | J4 | 56 | 5F27 | 39 | 2738 | 3338 | 13113 | All | 1
J457 | Motor Increase PID Control Start Frequency | ✔ | x | J4 | 57 | 5F27 | 3A | 2739 | 3339 | 13114 | All | 1
J458 | Motor Decrease Switching Time (Acceleration time) | ✔ | x | J4 | 58 | 5F27 | 3B | 273A | 333A | 13115 | All | 12
J459 | Motor Decrease Switching Level | ✔ | x | J4 | 59 | 5F27 | 3C | 273B | 333B | 13116 | All | 1
J460 | Motor Decrease PID Control Start Frequency | ✔ | x | J4 | 60 | 5F27 | 3D | 273C | 333C | 13117 | All | 1
J461 | Motor Increase/Decrease Switching Judgment Non-responsive Area Width | ✔ | x | J4 | 61 | 5F27 | 3E | 273D | 333D | 13118 | All | 3
J462 | Failure Inverter Judgment Time | ✔ | x | J4 | 62 | 5F27 | 3F | 273E | 333E | 13119 | All | 3
J465 | Auxiliary Motor (Frequency operation level) | ✔ | x | J4 | 65 | 5F27 | 42 | 2741 | 3341 | 13122 | All | 3
J466 | Auxiliary Motor (Hysteresis width) | ✔ | x | J4 | 66 | 5F27 | 43 | 2742 | 3342 | 13123 | All | 3
J467 | Auxiliary Motor (PV operation level) | ✔ | x | J4 | 67 | 5F27 | 44 | 2743 | 3343 | 13124 | All | 12
J468 | Auxiliary Motor (Connection timer) | ✔ | x | J4 | 68 | 5F27 | 45 | 2744 | 3344 | 13125 | All | 5
J469 | Auxiliary Motor (Interrupting timer) | ✔ | x | J4 | 69 | 5F27 | 46 | 2745 | 3345 | 13126 | All | 5
J480 | Motor Cumulative Run Time (Motor 0) | ✔ | x | J4 | 80 | 5F27 | 51 | 2750 | 3350 | 13137 | All | 1
J481 | Motor Cumulative Run Time (Motor 1) | ✔ | x | J4 | 81 | 5F27 | 52 | 2751 | 3351 | 13138 | All | 1
J482 | Motor Cumulative Run Time (Motor 2) | ✔ | x | J4 | 82 | 5F27 | 53 | 2752 | 3352 | 13139 | All | 1
J483 | Motor Cumulative Run Time (Motor 3) | ✔ | x | J4 | 83 | 5F27 | 54 | 2753 | 3353 | 13140 | All | 1
J484 | Motor Cumulative Run Time (Motor 4) | ✔ | x | J4 | 84 | 5F27 | 55 | 2754 | 3354 | 13141 | All | 1
J485 | Motor Cumulative Run Time (Motor 5) | ✔ | x | J4 | 85 | 5F27 | 56 | 2755 | 3355 | 13142 | All | 1
J486 | Motor Cumulative Run Time (Motor 6) | ✔ | x | J4 | 86 | 5F27 | 57 | 2756 | 3356 | 13143 | All | 1
J487 | Motor Cumulative Run Time (Motor 7) | ✔ | x | J4 | 87 | 5F27 | 58 | 2757 | 3357 | 13144 | All | 1
J488 | Motor Cumulative Run Time (Motor 8) | ✔ | x | J4 | 88 | 5F27 | 59 | 2758 | 3358 | 13145 | All | 1
J490 | Y Terminal ON Maximum Cumulation Count (Y1 Y2) | ✔ | x | J4 | 90 | 5F27 | 5B | 275A | 335A | 13147 | All | 45
J491 | Y Terminal ON Maximum Cumulation Count (Y3 Y4) | ✔ | x | J4 | 91 | 5F27 | 5C | 275B | 335B | 13148 | All | 45
J492 | Relay ON Maximum Cumulation Count (Y5A 30AB) | ✔ | x | J4 | 92 | 5F27 | 5D | 275C | 335C | 13149 | All | 45
J493 | Relay ON Maximum Cumulation Count (Y6RY to Y12RY) | ✔ | x | J4 | 93 | 5F27 | 5E | 275D | 335D | 13150 | All | 45
J501 | External PID Control 1 (Mode selection) | ✔ | ✔ | J5 | 01 | 5F28 | 02 | 2801 | 3401 | 13314 | All | 1
J502 | External PID Control 1 (Remote command selection) | ✔ | ✔ | J5 | 02 | 5F28 | 03 | 2802 | 3402 | 13315 | All | 1
J503 | External PID Control 1 (Feedback selection) | ✔ | ✔ | J5 | 03 | 5F28 | 04 | 2803 | 3403 | 13316 | All | 1
J504 | External PID Control 1 (Deviation selection) | ✔ | ✔ | J5 | 04 | 5F28 | 05 | 2804 | 3404 | 13317 | All | 1
J505 | External PID Control 1 (Display unit) | ✔ | ✔ | J5 | 05 | 5F28 | 06 | 2805 | 3405 | 13318 | All | 1
J506 | External PID Control 1 (Maximum scale) | ✔ | ✔ | J5 | 06 | 5F28 | 07 | 2806 | 3406 | 13319 | All | 12
J507 | External PID Control 1 (Minimum scale) | ✔ | ✔ | J5 | 07 | 5F28 | 08 | 2807 | 3407 | 13320 | All | 12
J510 | External PID Control 1 P (Gain) | ✔ | ✔ | J5 | 10 | 5F28 | 0B | 280A | 340A | 13323 | All | 7
J511 | External PID Control 1 I (Integral time) | ✔ | ✔ | J5 | 11 | 5F28 | 0C | 280B | 340B | 13324 | All | 3
J512 | External PID Control 1 D (Differential time) | ✔ | ✔ | J5 | 12 | 5F28 | 0D | 280C | 340C | 13325 | All | 5
J513 | External PID Control 1 (Feedback filter) | ✔ | ✔ | J5 | 13 | 5F28 | 0E | 280D | 340D | 13326 | All | 3
J514 | External PID Control 1 (Anti-reset wind-up) | ✔ | ✔ | J5 | 14 | 5F28 | 0F | 280E | 340E | 13327 | All | 12
J515 | External PID Control 1 (ON/OFF control hysteresis width) | ✔ | ✔ | J5 | 15 | 5F28 | 10 | 280F | 340F | 13328 | All | 12
J516 | External PID Control 1 (Proportional operation output convergent value) | ✔ | ✔ | J5 | 16 | 5F28 | 11 | 2810 | 3410 | 13329 | All | 1
J517 | External PID Control 1 (Proportional cycle) | ✔ | ✔ | J5 | 17 | 5F28 | 12 | 2811 | 3411 | 13330 | All | 1
J518 | External PID Control 1 (Upper limit of PID process output) | ✔ | ✔ | J5 | 18 | 5F28 | 13 | 2812 | 3412 | 13331 | All | 2
J519 | External PID Control 1 (Lower limit of PID process output) | ✔ | ✔ | J5 | 19 | 5F28 | 14 | 2813 | 3413 | 13332 | All | 2
J520 | External PID Control 1 (Upper and lower limits) | ✔ | ✔ | J5 | 20 | 5F28 | 15 | 2814 | 3414 | 13333 | All | 1
J521 | External PID Control 1 (Alarm output selection) | ✔ | ✔ | J5 | 21 | 5F28 | 16 | 2815 | 3415 | 13334 | All | 1
J522 | External PID Control 1 (Upper level alarm (AH)) | ✔ | ✔ | J5 | 22 | 5F28 | 17 | 2816 | 3416 | 13335 | All | 12
J524 | External PID Control 1 (Lower level alarm (AL)) | ✔ | ✔ | J5 | 24 | 5F28 | 19 | 2818 | 3418 | 13337 | All | 12
J527 | External PID Control 1 (Feedback error detection mode) | ✔ | ✔ | J5 | 27 | 5F28 | 1C | 281B | 341B | 13340 | All | 1
J529 | External PID Control 1 (Feedback error upper-limit) | ✔ | ✔ | J5 | 29 | 5F28 | 1E | 281D | 341D | 13342 | All | 12
J530 | External PID Control 1 (Feedback error lower-limit) | ✔ | ✔ | J5 | 30 | 5F28 | 1F | 281E | 341E | 13343 | All | 12
J531 | External PID Control 1 (Feedback error detection time) | ✔ | ✔ | J5 | 31 | 5F28 | 20 | 281F | 341F | 13344 | All | 3
J540 | External PID Control 1 (Manual command) | ✔ | ✔ | J5 | 40 | 5F28 | 29 | 2828 | 3428 | 13353 | All | 1
J550 | External PID Multistep Command (Mode selection) | ✔ | ✔ | J5 | 50 | 5F28 | 33 | 2832 | 3432 | 13363 | All | 1
J551 | External PID Multistep Command (Multistep command 1) | ✔ | ✔ | J5 | 51 | 5F28 | 34 | 2833 | 3433 | 13364 | All | 12
J552 | External PID Multistep Command (Multistep command 2) | ✔ | ✔ | J5 | 52 | 5F28 | 35 | 2834 | 3434 | 13365 | All | 12
J553 | External PID Multistep Command (Multistep command 3) | ✔ | ✔ | J5 | 53 | 5F28 | 36 | 2835 | 3435 | 13366 | All | 12
J601 | External PID Control 2 (Mode selection) | ✔ | ✔ | J6 | 01 | 5F29 | 02 | 2901 | 3501 | 13570 | All | 1
J602 | External PID Control 2 (Remote command selection) | ✔ | ✔ | J6 | 02 | 5F29 | 03 | 2902 | 3502 | 13571 | All | 1
J603 | External PID Control 2 (Feedback selection) | ✔ | ✔ | J6 | 03 | 5F29 | 04 | 2903 | 3503 | 13572 | All | 1
J605 | External PID Control 2 (Display unit) | ✔ | ✔ | J6 | 05 | 5F29 | 06 | 2905 | 3505 | 13574 | All | 1
J606 | External PID Control 2 (Maximum scale) | ✔ | ✔ | J6 | 06 | 5F29 | 07 | 2906 | 3506 | 13575 | All | 12
J607 | External PID Control 2 (Minimum scale) | ✔ | ✔ | J6 | 07 | 5F29 | 08 | 2907 | 3507 | 13576 | All | 12
J610 | External PID Control 2 P (Gain) | ✔ | ✔ | J6 | 10 | 5F29 | 0B | 290A | 350A | 13579 | All | 7
J611 | External PID Control 2 I (Integral time) | ✔ | ✔ | J6 | 11 | 5F29 | 0C | 290B | 350B | 13580 | All | 3
J612 | External PID Control 2 D (Differential time) | ✔ | ✔ | J6 | 12 | 5F29 | 0D | 290C | 350C | 13581 | All | 5
J613 | External PID Control 2 (Feedback filter) | ✔ | ✔ | J6 | 13 | 5F29 | 0E | 290D | 350D | 13582 | All | 3
J614 | External PID Control 2 (Anti-reset wind-up) | ✔ | ✔ | J6 | 14 | 5F29 | 0F | 290E | 350E | 13583 | All | 12
J615 | External PID Control 2 (ON/OFF control hysteresis width) | ✔ | ✔ | J6 | 15 | 5F29 | 10 | 290F | 350F | 13584 | All | 12
J616 | External PID Control 2 (Proportional operation output convergent value) | ✔ | ✔ | J6 | 16 | 5F29 | 11 | 2910 | 3510 | 13585 | All | 1
J617 | External PID Control 2 (Proportion cycle) | ✔ | ✔ | J6 | 17 | 5F29 | 12 | 2911 | 3511 | 13586 | All | 1
J618 | External PID Control 2 (Upper limit of PID process output) | ✔ | ✔ | J6 | 18 | 5F29 | 13 | 2912 | 3512 | 13587 | All | 2
J619 | External PID Control 2 (Lower limit of PID process output) | ✔ | ✔ | J6 | 19 | 5F29 | 14 | 2913 | 3513 | 13588 | All | 2
J620 | External PID Control 2 (Upper and lower limits) | ✔ | ✔ | J6 | 20 | 5F29 | 15 | 2914 | 3514 | 13589 | All | 1
J621 | External PID Control 2 (Alarm output selection) | ✔ | ✔ | J6 | 21 | 5F29 | 16 | 2915 | 3515 | 13590 | All | 1
J622 | External PID Control 2 (Upper level alarm (AH)) | ✔ | ✔ | J6 | 22 | 5F29 | 17 | 2916 | 3516 | 13591 | All | 12
J624 | External PID Control 2 (Lower level alarm (AL)) | ✔ | ✔ | J6 | 24 | 5F29 | 19 | 2918 | 3518 | 13593 | All | 12
J627 | External PID Control 2 (Feedback error detection mode) | ✔ | ✔ | J6 | 27 | 5F29 | 1C | 291B | 351B | 13596 | All | 1
J629 | External PID Control 2 (Feedback error upper-limit) | ✔ | ✔ | J6 | 29 | 5F29 | 1E | 291D | 351D | 13598 | All | 12
J630 | External PID Control 2 (Feedback error lower-limit) | ✔ | ✔ | J6 | 30 | 5F29 | 1F | 291E | 351E | 13599 | All | 12
J631 | External PID Control 2 (Feedback error detection time) | ✔ | ✔ | J6 | 31 | 5F29 | 20 | 291F | 351F | 13600 | All | 3
J640 | External PID Control 2 (Manual command) | ✔ | ✔ | J6 | 40 | 5F29 | 29 | 2928 | 3528 | 13609 | All | 1
J651 | External PID Control 3 (Mode selection) | ✔ | ✔ | J6 | 51 | 5F29 | 34 | 2933 | 3533 | 13620 | All | 1
J652 | External PID Control 3 (Remote command selection) | ✔ | ✔ | J6 | 52 | 5F29 | 35 | 2934 | 3534 | 13621 | All | 1
J653 | External PID Control 3 (Feedback selection) | ✔ | ✔ | J6 | 53 | 5F29 | 36 | 2935 | 3535 | 13622 | All | 1
J655 | External PID Control 3 (Display unit) | ✔ | ✔ | J6 | 55 | 5F29 | 38 | 2937 | 3537 | 13624 | All | 1
J656 | External PID Control 3 (Maximum scale) | ✔ | ✔ | J6 | 56 | 5F29 | 39 | 2938 | 3538 | 13625 | All | 12
J657 | External PID Control 3 (Minimum scale) | ✔ | ✔ | J6 | 57 | 5F29 | 3A | 2939 | 3539 | 13626 | All | 12
J660 | External PID Control 3 P (Gain) | ✔ | ✔ | J6 | 60 | 5F29 | 3D | 293C | 353C | 13629 | All | 7
J661 | External PID Control 3 I (Integral time) | ✔ | ✔ | J6 | 61 | 5F29 | 3E | 293D | 353D | 13630 | All | 3
J662 | External PID Control 3 D (Differential time) | ✔ | ✔ | J6 | 62 | 5F29 | 3F | 293E | 353E | 13631 | All | 5
J663 | External PID Control 3 (Feedback filter) | ✔ | ✔ | J6 | 63 | 5F29 | 40 | 293F | 353F | 13632 | All | 3
J664 | External PID Control 3 (Anti-reset wind-up) | ✔ | ✔ | J6 | 64 | 5F29 | 41 | 2940 | 3540 | 13633 | All | 12
J665 | External PID Control 3 (ON/OFF control hysteresis width) | ✔ | ✔ | J6 | 65 | 5F29 | 42 | 2941 | 3541 | 13634 | All | 12
J666 | External PID Control 3 (Proportional operation output convergent value) | ✔ | ✔ | J6 | 66 | 5F29 | 43 | 2942 | 3542 | 13635 | All | 1
J667 | External PID Control 3 (Proportion cycle) | ✔ | ✔ | J6 | 67 | 5F29 | 44 | 2943 | 3543 | 13636 | All | 1
J668 | External PID Control 3 (Upper limit of PID process output) | ✔ | ✔ | J6 | 68 | 5F29 | 45 | 2944 | 3544 | 13637 | All | 2
J669 | External PID Control 3 (Lower limit of PID process output) | ✔ | ✔ | J6 | 69 | 5F29 | 46 | 2945 | 3545 | 13638 | All | 2
J670 | External PID Control 3 (Upper and lower limits) | ✔ | ✔ | J6 | 70 | 5F29 | 47 | 2946 | 3546 | 13639 | All | 1
J671 | External PID Control 3 (Alarm output selection) | ✔ | ✔ | J6 | 71 | 5F29 | 48 | 2947 | 3547 | 13640 | All | 1
J672 | External PID Control 3 (Upper level alarm (AH)) | ✔ | ✔ | J6 | 72 | 5F29 | 49 | 2948 | 3548 | 13641 | All | 12
J674 | External PID Control 3 (Lower level alarm (AL)) | ✔ | ✔ | J6 | 74 | 5F29 | 4B | 294A | 354A | 13643 | All | 12
J677 | External PID Control 3 (Feedback error detection mode) | ✔ | ✔ | J6 | 77 | 5F29 | 4E | 294D | 354D | 13646 | All | 1
J679 | External PID Control 3 (Feedback error upper-limit) | ✔ | ✔ | J6 | 79 | 5F29 | 50 | 294F | 354F | 13648 | All | 12
J680 | External PID Control 3 (Feedback error lower-limit) | ✔ | ✔ | J6 | 80 | 5F29 | 51 | 2950 | 3550 | 13649 | All | 12
J681 | External PID Control 3 (Feedback error detection time) | ✔ | ✔ | J6 | 81 | 5F29 | 52 | 2951 | 3551 | 13650 | All | 3
J690 | External PID Control 3 (Manual commands) | ✔ | ✔ | J6 | 90 | 5F29 | 5B | 295A | 355A | 13659 | All | 1
d51 | Reserved | ✔ | ✔ | d | 51 | 5F14 | 34 | 1433 | 1333 | 4916 | All | 1
d55 | Reserved | ✔ | ✔ | d | 55 | 5F14 | 38 | 1437 | 1337 | 4920 | All | 1
d69 | Reserved | ✔ | ✔ | d | 69 | 5F14 | 46 | 1445 | 1345 | 4934 | All | 3
d98 | Reserved | ✔ | ✔ | d | 98 | 5F14 | 63 | 1462 | 1362 | 4963 | All | 1
d99 | Reserved | ✔ | ✔ | d | 99 | 5F14 | 64 | 1463 | 1363 | 4964 | All | 1
U00 | Customizable Logic (Mode selection) | ✔ | ✔ | U | 00 | 5F0D | 01 | 0D00 | 0B00 | 2817 | All | 1
U01 | Customizable Logic: Step 1 (Control function) | ✔ | ✔ | U | 01 | 5F0D | 02 | 0D01 | 0B01 | 2818 | All | 1
U02 | Customizable Logic: Step 1 (Input 1) | ✔ | ✔ | U | 02 | 5F0D | 03 | 0D02 | 0B02 | 2819 | All | 1
U03 | Customizable Logic: Step 1 (Input 2) | ✔ | ✔ | U | 03 | 5F0D | 04 | 0D03 | 0B03 | 2820 | All | 1
U04 | Customizable Logic: Step 1 (Function 1) | ✔ | ✔ | U | 04 | 5F0D | 05 | 0D04 | 0B04 | 2821 | All | 12
U05 | Customizable Logic: Step 1 (Function 2) | ✔ | ✔ | U | 05 | 5F0D | 06 | 0D05 | 0B05 | 2822 | All | 12
U06 | Customizable Logic: Step 2 (Control function) | ✔ | ✔ | U | 06 | 5F0D | 07 | 0D06 | 0B06 | 2823 | All | 1
U07 | Customizable Logic: Step 2 (Input 1) | ✔ | ✔ | U | 07 | 5F0D | 08 | 0D07 | 0B07 | 2824 | All | 1
U08 | Customizable Logic: Step 2 (Input 2) | ✔ | ✔ | U | 08 | 5F0D | 09 | 0D08 | 0B08 | 2825 | All | 1
U09 | Customizable Logic: Step 2 (Function 1) | ✔ | ✔ | U | 09 | 5F0D | 0A | 0D09 | 0B09 | 2826 | All | 12
U10 | Customizable Logic: Step 2 (Function 2) | ✔ | ✔ | U | 10 | 5F0D | 0B | 0D0A | 0B0A | 2827 | All | 12
U11 | Customizable Logic: Step 3 (Control function) | ✔ | ✔ | U | 11 | 5F0D | 0C | 0D0B | 0B0B | 2828 | All | 1
U12 | Customizable Logic: Step 3 (Input 1) | ✔ | ✔ | U | 12 | 5F0D | 0D | 0D0C | 0B0C | 2829 | All | 1
U13 | Customizable Logic: Step 3 (Input 2) | ✔ | ✔ | U | 13 | 5F0D | 0E | 0D0D | 0B0D | 2830 | All | 1
U14 | Customizable Logic: Step 3 (Function 1) | ✔ | ✔ | U | 14 | 5F0D | 0F | 0D0E | 0B0E | 2831 | All | 12
U15 | Customizable Logic: Step 3 (Function 2) | ✔ | ✔ | U | 15 | 5F0D | 10 | 0D0F | 0B0F | 2832 | All | 12
U16 | Customizable Logic: Step 4 (Control function) | ✔ | ✔ | U | 16 | 5F0D | 11 | 0D10 | 0B10 | 2833 | All | 1
U17 | Customizable Logic: Step 4 (Input 1) | ✔ | ✔ | U | 17 | 5F0D | 12 | 0D11 | 0B11 | 2834 | All | 1
U18 | Customizable Logic: Step 4 (Input 2) | ✔ | ✔ | U | 18 | 5F0D | 13 | 0D12 | 0B12 | 2835 | All | 1
U19 | Customizable Logic: Step 4 (Function 1) | ✔ | ✔ | U | 19 | 5F0D | 14 | 0D13 | 0B13 | 2836 | All | 12
U20 | Customizable Logic: Step 4 (Function 2) | ✔ | ✔ | U | 20 | 5F0D | 15 | 0D14 | 0B14 | 2837 | All | 12
U21 | Customizable Logic: Step 5 (Control function) | ✔ | ✔ | U | 21 | 5F0D | 16 | 0D15 | 0B15 | 2838 | All | 1
U22 | Customizable Logic: Step 5 (Input 1) | ✔ | ✔ | U | 22 | 5F0D | 17 | 0D16 | 0B16 | 2839 | All | 1
U23 | Customizable Logic: Step 5 (Input 2) | ✔ | ✔ | U | 23 | 5F0D | 18 | 0D17 | 0B17 | 2840 | All | 1
U24 | Customizable Logic: Step 5 (Function 1) | ✔ | ✔ | U | 24 | 5F0D | 19 | 0D18 | 0B18 | 2841 | All | 12
U25 | Customizable Logic: Step 5 (Function 2) | ✔ | ✔ | U | 25 | 5F0D | 1A | 0D19 | 0B19 | 2842 | All | 12
U26 | Customizable Logic: Step 6 (Control function) | ✔ | ✔ | U | 26 | 5F0D | 1B | 0D1A | 0B1A | 2843 | All | 1
U27 | Customizable Logic: Step 6 (Input 1) | ✔ | ✔ | U | 27 | 5F0D | 1C | 0D1B | 0B1B | 2844 | All | 1
U28 | Customizable Logic: Step 6 (Input 2) | ✔ | ✔ | U | 28 | 5F0D | 1D | 0D1C | 0B1C | 2845 | All | 1
U29 | Customizable Logic: Step 6 (Function 1) | ✔ | ✔ | U | 29 | 5F0D | 1E | 0D1D | 0B1D | 2846 | All | 12
U30 | Customizable Logic: Step 6 (Function 2) | ✔ | ✔ | U | 30 | 5F0D | 1F | 0D1E | 0B1E | 2847 | All | 12
U31 | Customizable Logic: Step 7 (Control function) | ✔ | ✔ | U | 31 | 5F0D | 20 | 0D1F | 0B1F | 2848 | All | 1
U32 | Customizable Logic: Step 7 (Input 1) | ✔ | ✔ | U | 32 | 5F0D | 21 | 0D20 | 0B20 | 2849 | All | 1
U33 | Customizable Logic: Step 7 (Input 2) | ✔ | ✔ | U | 33 | 5F0D | 22 | 0D21 | 0B21 | 2850 | All | 1
U34 | Customizable Logic: Step 7 (Function 1) | ✔ | ✔ | U | 34 | 5F0D | 23 | 0D22 | 0B22 | 2851 | All | 12
U35 | Customizable Logic: Step 7 (Function 2) | ✔ | ✔ | U | 35 | 5F0D | 24 | 0D23 | 0B23 | 2852 | All | 12
U36 | Customizable Logic: Step 8 (Control function) | ✔ | ✔ | U | 36 | 5F0D | 25 | 0D24 | 0B24 | 2853 | All | 1
U37 | Customizable Logic: Step 8 (Input 1) | ✔ | ✔ | U | 37 | 5F0D | 26 | 0D25 | 0B25 | 2854 | All | 1
U38 | Customizable Logic: Step 8 (Input 2) | ✔ | ✔ | U | 38 | 5F0D | 27 | 0D26 | 0B26 | 2855 | All | 1
U39 | Customizable Logic: Step 8 (Function 1) | ✔ | ✔ | U | 39 | 5F0D | 28 | 0D27 | 0B27 | 2856 | All | 12
U40 | Customizable Logic: Step 8 (Function 2) | ✔ | ✔ | U | 40 | 5F0D | 29 | 0D28 | 0B28 | 2857 | All | 12
U41 | Customizable Logic: Step 9 (Control function) | ✔ | ✔ | U | 41 | 5F0D | 2A | 0D29 | 0B29 | 2858 | All | 1
U42 | Customizable Logic: Step 9 (Input 1) | ✔ | ✔ | U | 42 | 5F0D | 2B | 0D2A | 0B2A | 2859 | All | 1
U43 | Customizable Logic: Step 9 (Input 2) | ✔ | ✔ | U | 43 | 5F0D | 2C | 0D2B | 0B2B | 2860 | All | 1
U44 | Customizable Logic: Step 9 (Function 1) | ✔ | ✔ | U | 44 | 5F0D | 2D | 0D2C | 0B2C | 2861 | All | 12
U45 | Customizable Logic: Step 9 (Function 2) | ✔ | ✔ | U | 45 | 5F0D | 2E | 0D2D | 0B2D | 2862 | All | 12
U46 | Customizable Logic: Step 10 (Control function) | ✔ | ✔ | U | 46 | 5F0D | 2F | 0D2E | 0B2E | 2863 | All | 1
U47 | Customizable Logic: Step 10 (Input 1) | ✔ | ✔ | U | 47 | 5F0D | 30 | 0D2F | 0B2F | 2864 | All | 1
U48 | Customizable Logic: Step 10 (Input 2) | ✔ | ✔ | U | 48 | 5F0D | 31 | 0D30 | 0B30 | 2865 | All | 1
U49 | Customizable Logic: Step 10 (Function 1) | ✔ | ✔ | U | 49 | 5F0D | 32 | 0D31 | 0B31 | 2866 | All | 12
U50 | Customizable Logic: Step 10 (Function 2) | ✔ | ✔ | U | 50 | 5F0D | 33 | 0D32 | 0B32 | 2867 | All | 12
U51 | Customizable Logic: Step 11 (Control function) | ✔ | ✔ | U | 51 | 5F0D | 34 | 0D33 | 0B33 | 2868 | All | 1
U52 | Customizable Logic: Step 11 (Input 1) | ✔ | ✔ | U | 52 | 5F0D | 35 | 0D34 | 0B34 | 2869 | All | 1
U53 | Customizable Logic: Step 11 (Input 2) | ✔ | ✔ | U | 53 | 5F0D | 36 | 0D35 | 0B35 | 2870 | All | 1
U54 | Customizable Logic: Step 11 (Function 1) | ✔ | ✔ | U | 54 | 5F0D | 37 | 0D36 | 0B36 | 2871 | All | 12
U55 | Customizable Logic: Step 11 (Function 2) | ✔ | ✔ | U | 55 | 5F0D | 38 | 0D37 | 0B37 | 2872 | All | 12
U56 | Customizable Logic: Step 12 (Control function) | ✔ | ✔ | U | 56 | 5F0D | 39 | 0D38 | 0B38 | 2873 | All | 1
U57 | Customizable Logic: Step 12 (Input 1) | ✔ | ✔ | U | 57 | 5F0D | 3A | 0D39 | 0B39 | 2874 | All | 1
U58 | Customizable Logic: Step 12 (Input 2) | ✔ | ✔ | U | 58 | 5F0D | 3B | 0D3A | 0B3A | 2875 | All | 1
U59 | Customizable Logic: Step 12 (Function 1) | ✔ | ✔ | U | 59 | 5F0D | 3C | 0D3B | 0B3B | 2876 | All | 12
U60 | Customizable Logic: Step 12 (Function 2) | ✔ | ✔ | U | 60 | 5F0D | 3D | 0D3C | 0B3C | 2877 | All | 12
U61 | Customizable Logic: Step 13 (Control function) | ✔ | ✔ | U | 61 | 5F0D | 3E | 0D3D | 0B3D | 2878 | All | 1
U62 | Customizable Logic: Step 13 (Input 1) | ✔ | ✔ | U | 62 | 5F0D | 3F | 0D3E | 0B3E | 2879 | All | 1
U63 | Customizable Logic: Step 13 (Input 2) | ✔ | ✔ | U | 63 | 5F0D | 40 | 0D3F | 0B3F | 2880 | All | 1
U64 | Customizable Logic: Step 13 (Function 1) | ✔ | ✔ | U | 64 | 5F0D | 41 | 0D40 | 0B40 | 2881 | All | 12
U65 | Customizable Logic: Step 13 (Function 2) | ✔ | ✔ | U | 65 | 5F0D | 42 | 0D41 | 0B41 | 2882 | All | 12
U66 | Customizable Logic: Step 14 (Control function) | ✔ | ✔ | U | 66 | 5F0D | 43 | 0D42 | 0B42 | 2883 | All | 1
U67 | Customizable Logic: Step 14 (Input 1) | ✔ | ✔ | U | 67 | 5F0D | 44 | 0D43 | 0B43 | 2884 | All | 1
U68 | Customizable Logic: Step 14 (Input 2) | ✔ | ✔ | U | 68 | 5F0D | 45 | 0D44 | 0B44 | 2885 | All | 1
U69 | Customizable Logic: Step 14 (Function 1) | ✔ | ✔ | U | 69 | 5F0D | 46 | 0D45 | 0B45 | 2886 | All | 12
U70 | Customizable Logic: Step 14 (Function 2) | ✔ | ✔ | U | 70 | 5F0D | 47 | 0D46 | 0B46 | 2887 | All | 12
U71 | Customizable Logic Output Signal 1 (Output selection) | ✔ | ✔ | U | 71 | 5F0D | 48 | 0D47 | 0B47 | 2888 | All | 1
U72 | Customizable Logic Output Signal 2 (Output selection) | ✔ | ✔ | U | 72 | 5F0D | 49 | 0D48 | 0B48 | 2889 | All | 1
U73 | Customizable Logic Output Signal 3 (Output selection) | ✔ | ✔ | U | 73 | 5F0D | 4A | 0D49 | 0B49 | 2890 | All | 1
U74 | Customizable Logic Output Signal 4 (Output selection) | ✔ | ✔ | U | 74 | 5F0D | 4B | 0D4A | 0B4A | 2891 | All | 1
U75 | Customizable Logic Output Signal 5 (Output selection) | ✔ | ✔ | U | 75 | 5F0D | 4C | 0D4B | 0B4B | 2892 | All | 1
U76 | Customizable Logic Output Signal 6 (Output selection) | ✔ | ✔ | U | 76 | 5F0D | 4D | 0D4C | 0B4C | 2893 | All | 1
U77 | Customizable Logic Output Signal 7 (Output selection) | ✔ | ✔ | U | 77 | 5F0D | 4E | 0D4D | 0B4D | 2894 | All | 1
U81 | Customizable Logic Output Signal 1 (Function selection) | ✔ | ✔ | U | 81 | 5F0D | 52 | 0D51 | 0B51 | 2898 | All | 1
U82 | Customizable Logic Output Signal 2 (Function selection) | ✔ | ✔ | U | 82 | 5F0D | 53 | 0D52 | 0B52 | 2899 | All | 1
U83 | Customizable Logic Output Signal 3 (Function selection) | ✔ | ✔ | U | 83 | 5F0D | 54 | 0D53 | 0B53 | 2900 | All | 1
U84 | Customizable Logic Output Signal 4 (Function selection) | ✔ | ✔ | U | 84 | 5F0D | 55 | 0D54 | 0B54 | 2901 | All | 1
U85 | Customizable Logic Output Signal 5 (Function selection) | ✔ | ✔ | U | 85 | 5F0D | 56 | 0D55 | 0B55 | 2902 | All | 1
U86 | Customizable Logic Output Signal 6 (Function selection) | ✔ | ✔ | U | 86 | 5F0D | 57 | 0D56 | 0B56 | 2903 | All | 1
U87 | Customizable Logic Output Signal 7 (Function selection) | ✔ | ✔ | U | 87 | 5F0D | 58 | 0D57 | 0B57 | 2904 | All | 1
U91 | Customizable Logic Timer Monitor (Step selection) | ✔ | ✔ | U | 91 | 5F0D | 5C | 0D5B | 0B5B | 2908 | All | 1
U92 | Customizable Logic Calculation Coefficient (Mantissa KA1) | ✔ | ✔ | U | 92 | 5F0D | 5D | 0D5C | 0B5C | 2909 | All | 8
U93 | Customizable Logic Calculation Coefficient (Exponent KA1) | ✔ | ✔ | U | 93 | 5F0D | 5E | 0D5D | 0B5D | 2910 | All | 2
U94 | Customizable Logic Calculation Coefficient (Mantissa KB1) | ✔ | ✔ | U | 94 | 5F0D | 5F | 0D5E | 0B5E | 2911 | All | 8
U95 | Customizable Logic Calculation Coefficient (Exponent KB1) | ✔ | ✔ | U | 95 | 5F0D | 60 | 0D5F | 0B5F | 2912 | All | 2
U96 | Customizable Logic Calculation Coefficient (Mantissa KC1) | ✔ | ✔ | U | 96 | 5F0D | 61 | 0D60 | 0B60 | 2913 | All | 8
U97 | Customizable Logic Calculation Coefficient (Exponent KC1) | ✔ | ✔ | U | 97 | 5F0D | 62 | 0D61 | 0B61 | 2914 | All | 2
U101 | Customizable Logic Conversion point 1 (X1) | ✔ | ✔ | U1 | 01 | 5F22 | 02 | 2201 | 2701 | 9986 | All | 12
U102 | Customizable Logic Conversion point 1 (Y1) | ✔ | ✔ | U1 | 02 | 5F22 | 03 | 2202 | 2702 | 9987 | All | 12
U103 | Customizable Logic Conversion point 2 (X2) | ✔ | ✔ | U1 | 03 | 5F22 | 04 | 2203 | 2703 | 9988 | All | 12
U104 | Customizable Logic Conversion point 2 (Y2) | ✔ | ✔ | U1 | 04 | 5F22 | 05 | 2204 | 2704 | 9989 | All | 12
U105 | Customizable Logic Conversion point 3 (X3) | ✔ | ✔ | U1 | 05 | 5F22 | 06 | 2205 | 2705 | 9990 | All | 12
U106 | Customizable Logic Conversion point 3 (Y3) | ✔ | ✔ | U1 | 06 | 5F22 | 07 | 2206 | 2706 | 9991 | All | 12
U107 | Automatic Calculation of Conversion Coefficients (X3) | ✔ | ✔ | U1 | 07 | 5F22 | 08 | 2207 | 2707 | 9992 | All | 1
y01 | RS-485 Communication 1 (Station address) | ✔ | ✔ | y | 01 | 5F0F | 02 | 0F01 | 0E01 | 3586 | All | 1
y02 | RS-485 Communication 1 (Communications error processing) | ✔ | ✔ | y | 02 | 5F0F | 03 | 0F02 | 0E02 | 3587 | All | 1
y03 | RS-485 Communication 1 (Timer) | ✔ | ✔ | y | 03 | 5F0F | 04 | 0F03 | 0E03 | 3588 | All | 3
y04 | RS-485 Communication 1 (Baud rate) | ✔ | ✔ | y | 04 | 5F0F | 05 | 0F04 | 0E04 | 3589 | All | 1
y05 | RS-485 Communication 1 (Data length) | ✔ | ✔ | y | 05 | 5F0F | 06 | 0F05 | 0E05 | 3590 | All | 1
y06 | RS-485 Communication 1 (Parity check) | ✔ | ✔ | y | 06 | 5F0F | 07 | 0F06 | 0E06 | 3591 | All | 1
y07 | RS-485 Communication 1 (Stop bits) | ✔ | ✔ | y | 07 | 5F0F | 08 | 0F07 | 0E07 | 3592 | All | 1
y08 | RS-485 Communication 1 (No response error detection time) | ✔ | ✔ | y | 08 | 5F0F | 09 | 0F08 | 0E08 | 3593 | All | 1
y09 | RS-485 Communication 1 (Response interval) | ✔ | ✔ | y | 09 | 5F0F | 0A | 0F09 | 0E09 | 3594 | All | 5
y10 | RS-485 Communication 1 (Protocol selection) | ✔ | ✔ | y | 10 | 5F0F | 0B | 0F0A | 0E0A | 3595 | All | 1
y11 | RS-485 Communication 2 (Station address) | ✔ | ✔ | y | 11 | 5F0F | 0C | 0F0B | 0E0B | 3596 | All | 1
y12 | RS-485 Communication 2 (Communications error processing) | ✔ | ✔ | y | 12 | 5F0F | 0D | 0F0C | 0E0C | 3597 | All | 1
y13 | RS-485 Communication 2 (Timer) | ✔ | ✔ | y | 13 | 5F0F | 0E | 0F0D | 0E0D | 3598 | All | 3
y14 | RS-485 Communication 2 (Baud rate) | ✔ | ✔ | y | 14 | 5F0F | 0F | 0F0E | 0E0E | 3599 | All | 1
y15 | RS-485 Communication 2 (Data length) | ✔ | ✔ | y | 15 | 5F0F | 10 | 0F0F | 0E0F | 3600 | All | 1
y16 | RS-485 Communication 2 (Parity check) | ✔ | ✔ | y | 16 | 5F0F | 11 | 0F10 | 0E10 | 3601 | All | 1
y17 | RS-485 Communication 2 (Stop bits) | ✔ | ✔ | y | 17 | 5F0F | 12 | 0F11 | 0E11 | 3602 | All | 1
y18 | RS-485 Communication 2 (No-response error detection time) | ✔ | ✔ | y | 18 | 5F0F | 13 | 0F12 | 0E12 | 3603 | All | 1
y19 | RS-485 Communication 2 (Response interval) | ✔ | ✔ | y | 19 | 5F0F | 14 | 0F13 | 0E13 | 3604 | All | 5
y20 | RS-485 Communication 2 (Protocol selection) | ✔ | ✔ | y | 20 | 5F0F | 15 | 0F14 | 0E14 | 3605 | All | 1
y60 | BACNet Device Instance (Upper) | ✔ | ✔ | y | 60 | 5F0F | 3D | 0F3C | 0E3C | 3645 | All | 1
y61 | BACNet Device Instance (Lower) | ✔ | ✔ | y | 61 | 5F0F | 3E | 0F3D | 0E3D | 3646 | All | 1
y95 | Data Clear Processing for Communications Error | ✔ | ✔ | y | 95 | 5F0F | 60 | 0F5F | 0E5F | 3680 | All | 1
y98 | Bus Link Function (Mode selection) | ✔ | ✔ | y | 98 | 5F0F | 63 | 0F62 | 0E62 | 3683 | All | 1
y99 | Loader Link Function (Mode selection) | ✔ | ✔ | y | 99 | 5F0F | 64 | 0F63 | 0E63 | 3684 | All | 1
o01 | Terminal [Y6A/B/C] Function | ✔ | ✔ | o | 01 | 5F0A | 02 | 0A01 | 0601 | 1538 | All | 1
o02 | Terminal [Y7A/B/C] Function | ✔ | ✔ | o | 02 | 5F0A | 03 | 0A02 | 0602 | 1539 | All | 1
o03 | Terminal [Y8A/B/C] Function | ✔ | ✔ | o | 03 | 5F0A | 04 | 0A03 | 0603 | 1540 | All | 1
o04 | Terminal [Y9A/B/C] Function | ✔ | ✔ | o | 04 | 5F0A | 05 | 0A04 | 0604 | 1541 | All | 1
o05 | Terminal [Y10A/B/C] Function | ✔ | ✔ | o | 05 | 5F0A | 06 | 0A05 | 0605 | 1542 | All | 1
o06 | Terminal [Y11A/B/C] Function | ✔ | ✔ | o | 06 | 5F0A | 07 | 0A06 | 0606 | 1543 | All | 1
o07 | Terminal [Y12A/B/C] Function | ✔ | ✔ | o | 07 | 5F0A | 08 | 0A07 | 0607 | 1544 | All | 1
o09 | Pt Channel (Display unit) | ✔ | ✔ | o | 09 | 5F0A | 0A | 0A09 | 0609 | 1546 | All | 1
o10 | Pt Channel 1 (Sensor type selection) | ✔ | ✔ | o | 10 | 5F0A | 0B | 0A0A | 060A | 1547 | All | 1
o11 | Pt Channel 1 (Extended Function) | ✔ | ✔ | o | 11 | 5F0A | 0C | 0A0B | 060B | 1548 | All | 1
o12 | Pt Channel 1 (Filter) | ✔ | ✔ | o | 12 | 5F0A | 0D | 0A0C | 060C | 1549 | All | 3
o15 | Pt Channel 2 (Sensor type selection) | ✔ | ✔ | o | 15 | 5F0A | 10 | 0A0F | 060F | 1552 | All | 1
o16 | Pt Channel 2 (Extended Function) | ✔ | ✔ | o | 16 | 5F0A | 11 | 0A10 | 0610 | 1553 | All | 1
o17 | Pt Channel 2 (Filter) | ✔ | ✔ | o | 17 | 5F0A | 12 | 0A11 | 0611 | 1554 | All | 3
o27 | Response error (Mode selection) | ✔ | ✔ | o | 27 | 5F0A | 1C | 0A1B | 061B | 1564 | All | 1
o28 | Response error (Timer) | ✔ | ✔ | o | 28 | 5F0A | 1D | 0A1C | 061C | 1565 | All | 3
o30 | Bus Parameter 01 | ✔ | ✔ | o | 30 | 5F0A | 1F | 0A1E | 061E | 1567 | All | 1
o31 | Bus Parameter 02 | ✔ | ✔ | o | 31 | 5F0A | 20 | 0A1F | 061F | 1568 | All | 1
o32 | Bus Parameter 03 | ✔ | ✔ | o | 32 | 5F0A | 21 | 0A20 | 0620 | 1569 | All | 1
o33 | Bus Parameter 04 | ✔ | ✔ | o | 33 | 5F0A | 22 | 0A21 | 0621 | 1570 | All | 1
o34 | Bus Parameter 05 | ✔ | ✔ | o | 34 | 5F0A | 23 | 0A22 | 0622 | 1571 | All | 1
o35 | Bus Parameter 06 | ✔ | ✔ | o | 35 | 5F0A | 24 | 0A23 | 0623 | 1572 | All | 1
o36 | Bus Parameter 07 | ✔ | ✔ | o | 36 | 5F0A | 25 | 0A24 | 0624 | 1573 | All | 1
o37 | Bus Parameter 08 | ✔ | ✔ | o | 37 | 5F0A | 26 | 0A25 | 0625 | 1574 | All | 1
o38 | Bus Parameter 09 | ✔ | ✔ | o | 38 | 5F0A | 27 | 0A26 | 0626 | 1575 | All | 1
o39 | Bus Parameter 10 | ✔ | ✔ | o | 39 | 5F0A | 28 | 0A27 | 0627 | 1576 | All | 1
o40 | Write Code 1 | ✔ | ✔ | o | 40 | 5F0A | 29 | 0A28 | 0628 | 1577 | All | 1
o41 | Write Code 2 | ✔ | ✔ | o | 41 | 5F0A | 2A | 0A29 | 0629 | 1578 | All | 1
o42 | Write Code 3 | ✔ | ✔ | o | 42 | 5F0A | 2B | 0A2A | 062A | 1579 | All | 1
o43 | Write Code 4 | ✔ | ✔ | o | 43 | 5F0A | 2C | 0A2B | 062B | 1580 | All | 1
o44 | Write Code 5 | ✔ | ✔ | o | 44 | 5F0A | 2D | 0A2C | 062C | 1581 | All | 1
o45 | Write Code 6 | ✔ | ✔ | o | 45 | 5F0A | 2E | 0A2D | 062D | 1582 | All | 1
o46 | Write Code 7 | ✔ | ✔ | o | 46 | 5F0A | 2F | 0A2E | 062E | 1583 | All | 1
o47 | Write Code 8 | ✔ | ✔ | o | 47 | 5F0A | 30 | 0A2F | 062F | 1584 | All | 1
o48 | Read Code 1 | ✔ | ✔ | o | 48 | 5F0A | 31 | 0A30 | 0630 | 1585 | All | 1
o49 | Read Code 2 | ✔ | ✔ | o | 49 | 5F0A | 32 | 0A31 | 0631 | 1586 | All | 1
o50 | Read Code 3 | ✔ | ✔ | o | 50 | 5F0A | 33 | 0A32 | 0632 | 1587 | All | 1
o51 | Read Code 4 | ✔ | ✔ | o | 51 | 5F0A | 34 | 0A33 | 0633 | 1588 | All | 1
o52 | Read Code 5 | ✔ | ✔ | o | 52 | 5F0A | 35 | 0A34 | 0634 | 1589 | All | 1
o53 | Read Code 6 | ✔ | ✔ | o | 53 | 5F0A | 36 | 0A35 | 0635 | 1590 | All | 1
o54 | Read Code 7 | ✔ | ✔ | o | 54 | 5F0A | 37 | 0A36 | 0636 | 1591 | All | 1
o55 | Read Code 8 | ✔ | ✔ | o | 55 | 5F0A | 38 | 0A37 | 0637 | 1592 | All | 1
o56 | Read Code 9 | ✔ | ✔ | o | 56 | 5F0A | 39 | 0A38 | 0638 | 1593 | All | 1
o57 | Read Code 10 | ✔ | ✔ | o | 57 | 5F0A | 3A | 0A39 | 0639 | 1594 | All | 1
o58 | Read Code 11 | ✔ | ✔ | o | 58 | 5F0A | 3B | 0A3A | 063A | 1595 | All | 1
o59 | Read Code 12 | ✔ | ✔ | o | 59 | 5F0A | 3C | 0A3B | 063B | 1596 | All | 1
o60 | Terminal [32] function (Mode selection) | ✔ | ✔ | o | 60 | 5F0A | 3D | 0A3C | 063C | 1597 | All | 1
o61 | Terminal [32] (Offset adjustment) | ✔ | ✔ | o | 61 | 5F0A | 3E | 0A3D | 063D | 1598 | All | 4
o62 | Terminal [32] (Gain adjustment) | ✔ | ✔ | o | 62 | 5F0A | 3F | 0A3E | 063E | 1599 | All | 5
o63 | Terminal [32] (Filter setting) | ✔ | ✔ | o | 63 | 5F0A | 40 | 0A3F | 063F | 1600 | All | 5
o64 | Terminal [32] (Gain base point) | ✔ | ✔ | o | 64 | 5F0A | 41 | 0A40 | 0640 | 1601 | All | 5
o65 | Terminal [32] (Polarity) | ✔ | ✔ | o | 65 | 5F0A | 42 | 0A41 | 0641 | 1602 | All | 1
o66 | Terminal [32] (Bias value) | ✔ | ✔ | o | 66 | 5F0A | 43 | 0A42 | 0642 | 1603 | All | 6
o67 | Terminal [32] (Gain base point) | ✔ | ✔ | o | 67 | 5F0A | 44 | 0A43 | 0643 | 1604 | All | 5
o69 | Terminal [32] (Display unit) | ✔ | ✔ | o | 69 | 5F0A | 46 | 0A45 | 0645 | 1606 | All | 1
o70 | Terminal [32] (Max scale) | ✔ | ✔ | o | 70 | 5F0A | 47 | 0A46 | 0646 | 1607 | All | 12
o71 | Terminal [32] (Min scale) | ✔ | ✔ | o | 71 | 5F0A | 48 | 0A47 | 0647 | 1608 | All | 12
o75 | Terminal [C2] (Range) | ✔ | ✔ | o | 75 | 5F0A | 4C | 0A4B | 064B | 1612 | All | 1
o76 | Terminal [C2] function (Mode selection) | ✔ | ✔ | o | 76 | 5F0A | 4D | 0A4C | 064C | 1613 | All | 1
o77 | Terminal [C2] (Offset adjustment) | ✔ | ✔ | o | 77 | 5F0A | 4E | 0A4D | 064D | 1614 | All | 4
o78 | Terminal [C2] (Gain adjustment) | ✔ | ✔ | o | 78 | 5F0A | 4F | 0A4E | 064E | 1615 | All | 5
o79 | Terminal [C2] (Filter setting) | ✔ | ✔ | o | 79 | 5F0A | 50 | 0A4F | 064F | 1616 | All | 5
o81 | Terminal [C2] (Gain base point) | ✔ | ✔ | o | 81 | 5F0A | 52 | 0A51 | 0651 | 1618 | All | 5
o82 | Terminal [C2] (Bias value) | ✔ | ✔ | o | 82 | 5F0A | 53 | 0A52 | 0652 | 1619 | All | 6
o83 | Terminal [C2] (Gain base point) | ✔ | ✔ | o | 83 | 5F0A | 54 | 0A53 | 0653 | 1620 | All | 5
o85 | Terminal [C2] (Display unit) | ✔ | ✔ | o | 85 | 5F0A | 56 | 0A55 | 0655 | 1622 | All | 1
o86 | Terminal [C2] (Max scale) | ✔ | ✔ | o | 86 | 5F0A | 57 | 0A56 | 0656 | 1623 | All | 12
o87 | Terminal [C2] (Min scale) | ✔ | ✔ | o | 87 | 5F0A | 58 | 0A57 | 0657 | 1624 | All | 12
o90 | Terminal [Ao/CS2] (Mode selection) | ✔ | ✔ | o | 90 | 5F0A | 5B | 0A5A | 065A | 1627 | All | 1
o91 | Terminal [Ao/CS2] (Voltage adjustment) | ✔ | ✔ | o | 91 | 5F0A | 5C | 0A5B | 065B | 1628 | All | 1
o93 | Terminal [Ao/CS2] (Polarity) | ✔ | ✔ | o | 93 | 5F0A | 5E | 0A5D | 065D | 1630 | All | 1
o96 | Terminal [CS/CS1] (Function) | ✔ | ✔ | o | 96 | 5F0A | 61 | 0A60 | 0660 | 1633 | All | 1
o97 | Terminal [CS/CS1] (Voltage adjustment) | ✔ | ✔ | o | 97 | 5F0A | 62 | 0A61 | 0661 | 1634 | All | 1
T01 | Timer 1 Operation (Operating mode) | ✔ | ✔ | T | 01 | 5F1E | 02 | 1E01 | 1D01 | 7426 | All | 1
T02 | Timer 1 Operation (Start time) | ✔ | ✔ | T | 02 | 5F1E | 03 | 1E02 | 1D02 | 7427 | All | 88
T03 | Timer 1 Operation (End time) | ✔ | ✔ | T | 03 | 5F1E | 04 | 1E03 | 1D03 | 7428 | All | 88
T04 | Timer 1 Operation (Start day of the week) | ✔ | ✔ | T | 04 | 5F1E | 05 | 1E04 | 1D04 | 7429 | All | 94
T06 | Timer 2 Operation (Operating mode) | ✔ | ✔ | T | 06 | 5F1E | 07 | 1E06 | 1D06 | 7431 | All | 1
T07 | Timer 2 Operation (Start time) | ✔ | ✔ | T | 07 | 5F1E | 08 | 1E07 | 1D07 | 7432 | All | 88
T08 | Timer 2 Operation (End time) | ✔ | ✔ | T | 08 | 5F1E | 09 | 1E08 | 1D08 | 7433 | All | 88
T09 | Timer 2 Operation (Start day of the week) | ✔ | ✔ | T | 09 | 5F1E | 0A | 1E09 | 1D09 | 7434 | All | 94
T11 | Timer 3 Operation (Operating mode) | ✔ | ✔ | T | 11 | 5F1E | 0C | 1E0B | 1D0B | 7436 | All | 1
T12 | Timer 3 Operation (Start time) | ✔ | ✔ | T | 12 | 5F1E | 0D | 1E0C | 1D0C | 7437 | All | 88
T13 | Timer 3 Operation (End time) | ✔ | ✔ | T | 13 | 5F1E | 0E | 1E0D | 1D0D | 7438 | All | 88
T14 | Timer 3 Operation (Start day of the week) | ✔ | ✔ | T | 14 | 5F1E | 0F | 1E0E | 1D0E | 7439 | All | 94
T16 | Timer 4 Operation (Operating mode) | ✔ | ✔ | T | 16 | 5F1E | 11 | 1E10 | 1D10 | 7441 | All | 1
T17 | Timer 4 Operation (Start time) | ✔ | ✔ | T | 17 | 5F1E | 12 | 1E11 | 1D11 | 7442 | All | 88
T18 | Timer 4 Operation (End time) | ✔ | ✔ | T | 18 | 5F1E | 13 | 1E12 | 1D12 | 7443 | All | 88
T19 | Timer 4 Operation (Start day of the week) | ✔ | ✔ | T | 19 | 5F1E | 14 | 1E13 | 1D13 | 7444 | All | 94
T51 | Timer Operation (Pause date 1) | ✔ | ✔ | T | 51 | 5F1E | 34 | 1E33 | 1D33 | 7476 | All | 89
T52 | Timer Operation (Pause date 2) | ✔ | ✔ | T | 52 | 5F1E | 35 | 1E34 | 1D34 | 7477 | All | 89
T53 | Timer Operation (Pause date 3) | ✔ | ✔ | T | 53 | 5F1E | 36 | 1E35 | 1D35 | 7478 | All | 89
T54 | Timer Operation (Pause date 4) | ✔ | ✔ | T | 54 | 5F1E | 37 | 1E36 | 1D36 | 7479 | All | 89
T55 | Timer Operation (Pause date 5) | ✔ | ✔ | T | 55 | 5F1E | 38 | 1E37 | 1D37 | 7480 | All | 89
T56 | Timer Operation (Pause date 6) | ✔ | ✔ | T | 56 | 5F1E | 39 | 1E38 | 1D38 | 7481 | All | 89
T57 | Timer Operation (Pause date 7) | ✔ | ✔ | T | 57 | 5F1E | 3A | 1E39 | 1D39 | 7482 | All | 89
T58 | Timer Operation (Pause date 8) | ✔ | ✔ | T | 58 | 5F1E | 3B | 1E3A | 1D3A | 7483 | All | 89
T59 | Timer Operation (Pause date 9) | ✔ | ✔ | T | 59 | 5F1E | 3C | 1E3B | 1D3B | 7484 | All | 89
T60 | Timer Operation (Pause date 10) | ✔ | ✔ | T | 60 | 5F1E | 3D | 1E3C | 1D3C | 7485 | All | 89
T61 | Timer Operation (Pause date 11) | ✔ | ✔ | T | 61 | 5F1E | 3E | 1E3D | 1D3D | 7486 | All | 89
T62 | Timer Operation (Pause date 12) | ✔ | ✔ | T | 62 | 5F1E | 3F | 1E3E | 1D3E | 7487 | All | 89
T63 | Timer Operation (Pause date 13) | ✔ | ✔ | T | 63 | 5F1E | 40 | 1E3F | 1D3F | 7488 | All | 89
T64 | Timer Operation (Pause date 14) | ✔ | ✔ | T | 64 | 5F1E | 41 | 1E40 | 1D40 | 7489 | All | 89
T65 | Timer Operation (Pause date 15) | ✔ | ✔ | T | 65 | 5F1E | 42 | 1E41 | 1D41 | 7490 | All | 89
T66 | Timer Operation (Pause date 16) | ✔ | ✔ | T | 66 | 5F1E | 43 | 1E42 | 1D42 | 7491 | All | 89
T67 | Timer Operation (Pause date 17) | ✔ | ✔ | T | 67 | 5F1E | 44 | 1E43 | 1D43 | 7492 | All | 89
T68 | Timer Operation (Pause date 18) | ✔ | ✔ | T | 68 | 5F1E | 45 | 1E44 | 1D44 | 7493 | All | 89
T69 | Timer Operation (Pause date 19) | ✔ | ✔ | T | 69 | 5F1E | 46 | 1E45 | 1D45 | 7494 | All | 89
T70 | Timer Operation (Pause date 20) | ✔ | ✔ | T | 70 | 5F1E | 47 | 1E46 | 1D46 | 7495 | All | 89
K01 | LCD Monitor (Language selection) | ✔ | ✔ | K | 01 | 5F1D | 02 | 1D01 | 1C01 | 7170 | All | 1
K02 | Backlight OFF Time | ✔ | ✔ | K | 02 | 5F1D | 03 | 1D02 | 1C02 | 7171 | All | 1
K03 | LCD Monitor (Backlight brightness control) | ✔ | ✔ | K | 03 | 5F1D | 04 | 1D03 | 1C03 | 7172 | All | 1
K04 | LCD Monitor (Contrast control) | ✔ | ✔ | K | 04 | 5F1D | 05 | 1D04 | 1C04 | 7173 | All | 1
K08 | LCD Monitor Status Display/Hide Selection | ✔ | ✔ | K | 08 | 5F1D | 09 | 1D08 | 1C08 | 7177 | All | 1
K10 | Main Monitor (Display item selection) | ✔ | ✔ | K | 10 | 5F1D | 0B | 1D0A | 1C0A | 7179 | All | 1
K11 | Main Monitor (Speed monitor item) | ✔ | ✔ | K | 11 | 5F1D | 0C | 1D0B | 1C0B | 7180 | All | 1
K12 | Main Monitor (Display when stopped) | ✔ | ✔ | K | 12 | 5F1D | 0D | 1D0C | 1C0C | 7181 | All | 1
K15 | Sub Monitor (Display type) | ✔ | ✔ | K | 15 | 5F1D | 10 | 1D0F | 1C0F | 7184 | All | 1
K16 | Sub Monitor 1 (Display item selection) | ✔ | ✔ | K | 16 | 5F1D | 11 | 1D10 | 1C10 | 7185 | All | 1
K17 | Sub Monitor 2 (Display item selection) | ✔ | ✔ | K | 17 | 5F1D | 12 | 1D11 | 1C11 | 7186 | All | 1
K20 | Bar Chart 1 (Display item selection) | ✔ | ✔ | K | 20 | 5F1D | 15 | 1D14 | 1C14 | 7189 | All | 1
K21 | Bar Chart 2 (Display item selection) | ✔ | ✔ | K | 21 | 5F1D | 16 | 1D15 | 1C15 | 7190 | All | 1
K22 | Bar Chart 3 (Display item selection) | ✔ | ✔ | K | 22 | 5F1D | 17 | 1D16 | 1C16 | 7191 | All | 1
K29 | Display Filter | ✔ | ✔ | K | 29 | 5F1D | 1E | 1D1D | 1C1D | 7198 | All | 3
K30 | Coefficient for Speed Indication | ✔ | ✔ | K | 30 | 5F1D | 1F | 1D1E | 1C1E | 7199 | All | 5
K31 | Display Unit for Input Watt-hour Data | ✔ | ✔ | K | 31 | 5F1D | 20 | 1D1F | 1C1F | 7200 | All | 1
K32 | Display Coefficient for Input Watt-hour Data | ✔ | ✔ | K | 32 | 5F1D | 21 | 1D20 | 1C20 | 7201 | All | 45
K33 | Long-term Input Watt-hour Data Monitor | ✔ | ✔ | K | 33 | 5F1D | 22 | 1D21 | 1C21 | 7202 | All | 1
K81 | Date Format | ✔ | ✔ | K | 81 | 5F1D | 52 | 1D51 | 1C51 | 7250 | All | 1
K82 | Time Format | ✔ | ✔ | K | 82 | 5F1D | 53 | 1D52 | 1C52 | 7251 | All | 1
K83 | Daylight Saving Time (Summer time) | ✔ | ✔ | K | 83 | 5F1D | 54 | 1D53 | 1C53 | 7252 | All | 1
K84 | Daylight Saving Time (Start date) | ✔ | ✔ | K | 84 | 5F1D | 55 | 1D54 | 1C54 | 7253 | All | 90
K85 | Daylight Saving Time (End date) | ✔ | ✔ | K | 85 | 5F1D | 56 | 1D55 | 1C55 | 7254 | All | 90
K91 | Shortcut Key Function for < in Running Mode (Selection screen) | ✔ | ✔ | K | 91 | 5F1D | 5C | 1D5B | 1C5B | 7260 | All | 1
K92 | Shortcut Key Function for > in Running Mode (Selection screen) | ✔ | ✔ | K | 92 | 5F1D | 5D | 1D5C | 1C5C | 7261 | All | 1
S01 | Frequency reference (p.u.) | ✔ | ✔ | S | 01 | 5F02 | 02 | 0201 | 0701 | 1794 | All | 29
S05 | Frequency reference | ✔ | ✔ | S | 05 | 5F02 | 06 | 0205 | 0705 | 1798 | All | 22
S06 | Operation command | ✔ | ✔ | S | 06 | 5F02 | 07 | 0206 | 0706 | 1799 | All | 14
S07 | Universal DO | ✔ | ✔ | S | 07 | 5F02 | 08 | 0207 | 0707 | 1800 | All | 15
S08 | Acceleration time F07 | ✔ | ✔ | S | 08 | 5F02 | 09 | 0208 | 0708 | 1801 | All | 3
S09 | Deceleration time F08 | ✔ | ✔ | S | 09 | 5F02 | 0A | 0209 | 0709 | 1802 | All | 3
S10 | Torque Limiter 1 | ✔ | ✔ | S | 10 | 5F02 | 0B | 020A | 070A | 1803 | All | 6
S11 | Torque Limiter 2 | ✔ | ✔ | S | 11 | 5F02 | 0C | 020B | 070B | 1804 | All | 6
S12 | Universal Ao | ✔ | ✔ | S | 12 | 5F02 | 0D | 020C | 070C | 1805 | All | 29
S13 | PID command | ✔ | ✔ | S | 13 | 5F02 | 0E | 020D | 070D | 1806 | All | 29
S14 | Alarm reset command | ✔ | ✔ | S | 14 | 5F02 | 0F | 020E | 070E | 1807 | All | 1
S19 | Rotation speed command | ✔ | ✔ | S | 19 | 5F02 | 14 | 0213 | 0713 | 1812 | All | 2
S31 | External PID command 1 | ✔ | ✔ | S | 31 | 5F02 | 20 | 021F | 071F | 1824 | All | 29
S32 | External PID command 2 | ✔ | ✔ | S | 32 | 5F02 | 21 | 0220 | 0720 | 1825 | All | 29
S33 | External PID command 3 | ✔ | ✔ | S | 33 | 5F02 | 22 | 0221 | 0721 | 1826 | All | 29
S90 | Present date(Year/Month) | ✔ | ✔ | S | 90 | 5F02 | 5B | 025A | 075A | 1883 | All | 85
S91 | Present date(Day/Hour) | ✔ | ✔ | S | 91 | 5F02 | 5C | 025B | 075B | 1884 | All | 86
S92 | Present date(Minute/Second) | ✔ | ✔ | S | 92 | 5F02 | 5D | 025C | 075C | 1885 | All | 87
S93 | Match at clock time | ✔ | ✔ | S | 93 | 5F02 | 5E | 025D | 075D | 1886 | All | 1
M01 | Frequency reference (p.u.) (Final command) | ✔ | ✔ | M | 01 | 5F03 | 02 | 0301 | 0801 | 2050 | All | 29
M05 | Frequency reference (Final command) | ✔ | ✔ | M | 05 | 5F03 | 06 | 0305 | 0805 | 2054 | All | 22
M06 | Output frequency 1(p.u.) | ✔ | ✔ | M | 06 | 5F03 | 07 | 0306 | 0806 | 2055 | All | 29
M07 | Torque real value | ✔ | ✔ | M | 07 | 5F03 | 08 | 0307 | 0807 | 2056 | All | 6
M09 | Output frequency | ✔ | ✔ | M | 09 | 5F03 | 0A | 0309 | 0809 | 2058 | FGI | 23
M09 | Output frequency | ✔ | ✔ | M | 09 | 5F03 | 0A | 0309 | 0809 | 2058 | RTU | 22
M09 | Output frequency | ✔ | ✔ | M | 09 | 5F03 | 0A | 0309 | 0809 | 2058 | BUS | 22
M10 | Input power | ✔ | ✔ | M | 10 | 5F03 | 0B | 030A | 080A | 2059 | All | 5
M11 | Output current effective value | ✔ | ✔ | M | 11 | 5F03 | 0C | 030B | 080B | 2060 | All | 5
M12 | Output voltage effective value | ✔ | ✔ | M | 12 | 5F03 | 0D | 030C | 080C | 2061 | All | 3
M13 | Operation command (Final command) | ✔ | ✔ | M | 13 | 5F03 | 0E | 030D | 080D | 2062 | All | 14
M14 | Operation status | ✔ | ✔ | M | 14 | 5F03 | 0F | 030E | 080E | 2063 | All | 16
M15 | General-purpose output terminal information | ✔ | ✔ | M | 15 | 5F03 | 10 | 030F | 080F | 2064 | All | 15
M16 | Latest alarm contents | ✔ | ✔ | M | 16 | 5F03 | 11 | 0310 | 0810 | 2065 | All | 10
M17 | Last alarm contents | ✔ | ✔ | M | 17 | 5F03 | 12 | 0311 | 0811 | 2066 | All | 10
M18 | Second last alarm contents | ✔ | ✔ | M | 18 | 5F03 | 13 | 0312 | 0812 | 2067 | All | 10
M19 | Third last alarm contents | ✔ | ✔ | M | 19 | 5F03 | 14 | 0313 | 0813 | 2068 | All | 10
M20 | Cumulative operation time | ✔ | ✔ | M | 20 | 5F03 | 15 | 0314 | 0814 | 2069 | All | 1
M21 | DC link circuit voltage | ✔ | ✔ | M | 21 | 5F03 | 16 | 0315 | 0815 | 2070 | All | 1
M23 | Model code | ✔ | ✔ | M | 23 | 5F03 | 18 | 0317 | 0817 | 2072 | All | 17
M24 | Capacity code | ✔ | ✔ | M | 24 | 5F03 | 19 | 0318 | 0818 | 2073 | All | 11
M25 | ROM version | ✔ | ✔ | M | 25 | 5F03 | 1A | 0319 | 0819 | 2074 | All | 35
M26 | Transmission error transaction code | ✔ | ✔ | M | 26 | 5F03 | 1B | 031A | 081A | 2075 | All | 20
M27 | Frequency reference on alarm (p.u.) (Final command) | ✔ | ✔ | M | 27 | 5F03 | 1C | 031B | 081B | 2076 | All | 29
M31 | Frequency reference on alarm (Final command) | ✔ | ✔ | M | 31 | 5F03 | 20 | 031F | 081F | 2080 | All | 22
M32 | Output frequency 1 on alarm (p.u.) | ✔ | ✔ | M | 32 | 5F03 | 21 | 0320 | 0820 | 2081 | All | 29
M33 | Torque value on alarm | ✔ | ✔ | M | 33 | 5F03 | 22 | 0321 | 0821 | 2082 | All | 6
M35 | Output frequency on alarm | ✔ | ✔ | M | 35 | 5F03 | 24 | 0323 | 0823 | 2084 | FGI | 23
M35 | Output frequency on alarm | ✔ | ✔ | M | 35 | 5F03 | 24 | 0323 | 0823 | 2084 | RTU | 22
M35 | Output frequency on alarm | ✔ | ✔ | M | 35 | 5F03 | 24 | 0323 | 0823 | 2084 | BUS | 22
M36 | Input power on alarm | ✔ | ✔ | M | 36 | 5F03 | 25 | 0324 | 0824 | 2085 | All | 5
M37 | Output current effective value on alarm | ✔ | ✔ | M | 37 | 5F03 | 26 | 0325 | 0825 | 2086 | All | 5
M38 | Output voltage effective value on alarm | ✔ | ✔ | M | 38 | 5F03 | 27 | 0326 | 0826 | 2087 | All | 3
M39 | Operation command on alarm | ✔ | ✔ | M | 39 | 5F03 | 28 | 0327 | 0827 | 2088 | All | 14
M40 | Operation status on alarm | ✔ | ✔ | M | 40 | 5F03 | 29 | 0328 | 0828 | 2089 | All | 16
M41 | Output terminal information on alarm | ✔ | ✔ | M | 41 | 5F03 | 2A | 0329 | 0829 | 2090 | All | 15
M42 | Cumulative operation time on alarm | ✔ | ✔ | M | 42 | 5F03 | 2B | 032A | 082A | 2091 | All | 1
M43 | DC link circuit voltage on alarm | ✔ | ✔ | M | 43 | 5F03 | 2C | 032B | 082B | 2092 | All | 1
M44 | Inverter internal air temperature on alarm | ✔ | ✔ | M | 44 | 5F03 | 2D | 032C | 082C | 2093 | All | 1
M45 | Heat sink temperature on alarm | ✔ | ✔ | M | 45 | 5F03 | 2E | 032D | 082D | 2094 | All | 1
M46 | Life of main circuit capacitor | ✔ | ✔ | M | 46 | 5F03 | 2F | 032E | 082E | 2095 | All | 3
M47 | Life of PC board electrolytic capacitor | ✔ | ✔ | M | 47 | 5F03 | 30 | 032F | 082F | 2096 | All | 74
M48 | Life of cooling fan | ✔ | ✔ | M | 48 | 5F03 | 31 | 0330 | 0830 | 2097 | All | 74
M49 | Input terminal voltage[12] (p.u.) | ✔ | ✔ | M | 49 | 5F03 | 32 | 0331 | 0831 | 2098 | All | 29
M50 | Input terminal current[C1] (p.u.) | ✔ | ✔ | M | 50 | 5F03 | 33 | 0332 | 0832 | 2099 | All | 29
M52 | Input terminal voltage[32] | ✔ | ✔ | M | 52 | 5F03 | 35 | 0334 | 0834 | 2101 | All | 29
M53 | Input terminal current[C2] | ✔ | ✔ | M | 53 | 5F03 | 36 | 0335 | 0835 | 2102 | All | 29
M54 | Input terminal voltage[V2] (p.u.) | ✔ | ✔ | M | 54 | 5F03 | 37 | 0336 | 0836 | 2103 | All | 29
M61 | Inverter internal air temperature | ✔ | ✔ | M | 61 | 5F03 | 3E | 033D | 083D | 2110 | All | 1
M62 | Heat sink temperature | ✔ | ✔ | M | 62 | 5F03 | 3F | 033E | 083E | 2111 | All | 1
M63 | Load rate | ✔ | ✔ | M | 63 | 5F03 | 40 | 033F | 083F | 2112 | All | 6
M64 | Motor output | ✔ | ✔ | M | 64 | 5F03 | 41 | 0340 | 0840 | 2113 | All | 6
M65 | Motor output on alarm | ✔ | ✔ | M | 65 | 5F03 | 42 | 0341 | 0841 | 2114 | All | 29
M66 | Speed detection | ✔ | ✔ | M | 66 | 5F03 | 43 | 0342 | 0842 | 2115 | All | 29
M67 | Transmission error handling code 2 | ✔ | ✔ | M | 67 | 5F03 | 44 | 0343 | 0843 | 2116 | All | 20
M68 | PID final command | ✔ | ✔ | M | 68 | 5F03 | 45 | 0344 | 0844 | 2117 | All | 29
M69 | Inverter rated current | ✔ | ✔ | M | 69 | 5F03 | 46 | 0345 | 0845 | 2118 | FGI | 24
M69 | Inverter rated current | ✔ | ✔ | M | 69 | 5F03 | 46 | 0345 | 0845 | 2118 | RTU | 19
M69 | Inverter rated current | ✔ | ✔ | M | 69 | 5F03 | 46 | 0345 | 0845 | 2118 | BUS | 24
M70 | Operation status 2 | ✔ | ✔ | M | 70 | 5F03 | 47 | 0346 | 0846 | 2119 | All | 44
M71 | Input terminal information | ✔ | ✔ | M | 71 | 5F03 | 48 | 0347 | 0847 | 2120 | All | 14
M72 | PID feedback value | ✔ | ✔ | M | 72 | 5F03 | 49 | 0348 | 0848 | 2121 | All | 29
M73 | PID output | ✔ | ✔ | M | 73 | 5F03 | 4A | 0349 | 0849 | 2122 | All | 29
M74 | Operating status 2 | ✔ | ✔ | M | 74 | 5F03 | 4B | 034A | 084A | 2123 | All | 76
M76 | Main circuit capacity life (Elapsed time) | ✔ | ✔ | M | 76 | 5F03 | 4D | 034C | 084C | 2125 | All | 74
M77 | Main circuit capacity life (Remaining time) | ✔ | ✔ | M | 77 | 5F03 | 4E | 034D | 084D | 2126 | All | 74
M78 | Rotation speed command | ✔ | ✔ | M | 78 | 5F03 | 4F | 034E | 084E | 2127 | All | 2
M79 | Rotation speed | ✔ | ✔ | M | 79 | 5F03 | 50 | 034F | 084F | 2128 | All | 2
M81 | Maintenance (Remaining time) (M1) | ✔ | ✔ | M | 81 | 5F03 | 52 | 0351 | 0851 | 2130 | All | 74
M85 | Maintenance (Starting times) (M1) | ✔ | ✔ | M | 85 | 5F03 | 56 | 0355 | 0855 | 2134 | All | 1
M86 | Light alarm contents (Latest) | ✔ | ✔ | M | 86 | 5F03 | 57 | 0356 | 0856 | 2135 | All | 41
M87 | Light alarm contents (Last) | ✔ | ✔ | M | 87 | 5F03 | 58 | 0357 | 0857 | 2136 | All | 41
M88 | Light alarm contents (Second last) | ✔ | ✔ | M | 88 | 5F03 | 59 | 0358 | 0858 | 2137 | All | 41
M89 | Light alarm contents (Third last) | ✔ | ✔ | M | 89 | 5F03 | 5A | 0359 | 0859 | 2138 | All | 41
W01 | Operation status | ✔ | ✔ | W | 01 | 5F10 | 02 | 1001 | 0F01 | 3842 | All | 16
W02 | Frequency reference | ✔ | ✔ | W | 02 | 5F10 | 03 | 1002 | 0F02 | 3843 | All | 22
W03 | Output frequency (before slip compensation) | ✔ | ✔ | W | 03 | 5F10 | 04 | 1003 | 0F03 | 3844 | All | 22
W04 | Output frequency (after slip compensation) | ✔ | ✔ | W | 04 | 5F10 | 05 | 1004 | 0F04 | 3845 | All | 22
W05 | Output current | ✔ | ✔ | W | 05 | 5F10 | 06 | 1005 | 0F05 | 3846 | FGI | 24
W05 | Output current | ✔ | ✔ | W | 05 | 5F10 | 06 | 1005 | 0F05 | 3846 | RTU | 19
W05 | Output current | ✔ | ✔ | W | 05 | 5F10 | 06 | 1005 | 0F05 | 3846 | BUS | 24
W06 | Output voltage | ✔ | ✔ | W | 06 | 5F10 | 07 | 1006 | 0F06 | 3847 | All | 3
W07 | Torque | ✔ | ✔ | W | 07 | 5F10 | 08 | 1007 | 0F07 | 3848 | All | 2
W08 | Motor speed | ✔ | ✔ | W | 08 | 5F10 | 09 | 1008 | 0F08 | 3849 | All | 37
W09 | Load rotation speed | ✔ | ✔ | W | 09 | 5F10 | 0A | 1009 | 0F09 | 3850 | All | 37
W11 | PID process command | ✔ | ✔ | W | 11 | 5F10 | 0C | 100B | 0F0B | 3852 | All | 12
W12 | PID feedback value | ✔ | ✔ | W | 12 | 5F10 | 0D | 100C | 0F0C | 3853 | All | 12
W13 | Level of torque value A | ✔ | ✔ | W | 13 | 5F10 | 0E | 100D | 0F0D | 3854 | All | 2
W14 | Level of torque value B | ✔ | ✔ | W | 14 | 5F10 | 0F | 100E | 0F0E | 3855 | All | 2
W16 | Rotation speed set value | ✔ | ✔ | W | 16 | 5F10 | 11 | 1010 | 0F10 | 3857 | All | 37
W17 | Load speed set value | ✔ | ✔ | W | 17 | 5F10 | 12 | 1011 | 0F11 | 3858 | All | 37
W21 | Input power | ✔ | ✔ | W | 21 | 5F10 | 16 | 1015 | 0F15 | 3862 | All | 24
W22 | Motor output | ✔ | ✔ | W | 22 | 5F10 | 17 | 1016 | 0F16 | 3863 | All | 24
W23 | Load rate | ✔ | ✔ | W | 23 | 5F10 | 18 | 1017 | 0F17 | 3864 | All | 2
W28 | Operation command source | ✔ | ✔ | W | 28 | 5F10 | 1D | 101C | 0F1C | 3869 | All | 67
W29 | Frequency and PID command source | ✔ | ✔ | W | 29 | 5F10 | 1E | 101D | 0F1D | 3870 | All | 68
W30 | Speed at percentage | ✔ | ✔ | W | 30 | 5F10 | 1F | 101E | 0F1E | 3871 | All | 5
W31 | Speed set value at percentage | ✔ | ✔ | W | 31 | 5F10 | 20 | 101F | 0F1F | 3872 | All | 5
W32 | PID output | ✔ | ✔ | W | 32 | 5F10 | 21 | 1020 | 0F20 | 3873 | All | 4
W33 | Analog input monitor | ✔ | ✔ | W | 33 | 5F10 | 22 | 1021 | 0F21 | 3874 | All | 12
W35 | Terminal [32] input voltage | ✔ | ✔ | W | 35 | 5F10 | 24 | 1023 | 0F23 | 3876 | All | 4
W36 | Terminal [C2] input current | ✔ | ✔ | W | 36 | 5F10 | 25 | 1024 | 0F24 | 3877 | All | 4
W37 | Terminal [AO] output voltage | ✔ | ✔ | W | 37 | 5F10 | 26 | 1025 | 0F25 | 3878 | All | 4
W38 | Terminal [CS] output current | ✔ | ✔ | W | 38 | 5F10 | 27 | 1026 | 0F26 | 3879 | All | 3
W40 | Control circuit terminal (input) | ✔ | ✔ | W | 40 | 5F10 | 29 | 1028 | 0F28 | 3881 | All | 43
W41 | Control circuit terminal (output) | ✔ | ✔ | W | 41 | 5F10 | 2A | 1029 | 0F29 | 3882 | All | 15
W42 | Communications control signal (input) | ✔ | ✔ | W | 42 | 5F10 | 2B | 102A | 0F2A | 3883 | All | 14
W43 | Communications control signal (output) | ✔ | ✔ | W | 43 | 5F10 | 2C | 102B | 0F2B | 3884 | All | 15
W44 | Terminal [12] input voltage | ✔ | ✔ | W | 44 | 5F10 | 2D | 102C | 0F2C | 3885 | All | 4
W45 | Terminal [C1] input current | ✔ | ✔ | W | 45 | 5F10 | 2E | 102D | 0F2D | 3886 | All | 4
W46 | Terminal [FM 1] output voltage | ✔ | ✔ | W | 46 | 5F10 | 2F | 102E | 0F2E | 3887 | All | 3
W47 | Terminal [FM 2] output voltage | ✔ | ✔ | W | 47 | 5F10 | 30 | 102F | 0F2F | 3888 | All | 3
W49 | Terminal [V2] input voltage | ✔ | ✔ | W | 49 | 5F10 | 32 | 1031 | 0F31 | 3890 | All | 4
W50 | Terminal [FM 1] output current | ✔ | ✔ | W | 50 | 5F10 | 33 | 1032 | 0F32 | 3891 | All | 3
W65 | Terminal [FM 2] output current | ✔ | ✔ | W | 65 | 5F10 | 42 | 1041 | 0F41 | 3906 | All | 3
W67 | Cumulative operation time of electrolytic | ✔ | ✔ | W | 67 | 5F10 | 44 | 1043 | 0F43 | 3908 | All | 74
W68 | Cumulative operation time of cooling fan | ✔ | ✔ | W | 68 | 5F10 | 45 | 1044 | 0F44 | 3909 | All | 74
W70 | Cumulative operation time | ✔ | ✔ | W | 70 | 5F10 | 47 | 1046 | 0F46 | 3911 | All | 1
W71 | DC link circuit voltage | ✔ | ✔ | W | 71 | 5F10 | 48 | 1047 | 0F47 | 3912 | All | 1
W72 | Internal air highest temperature | ✔ | ✔ | W | 72 | 5F10 | 49 | 1048 | 0F48 | 3913 | All | 1
W73 | Heat sink maximum temperature | ✔ | ✔ | W | 73 | 5F10 | 4A | 1049 | 0F49 | 3914 | All | 1
W74 | Maximum effective current value | ✔ | ✔ | W | 74 | 5F10 | 4B | 104A | 0F4A | 3915 | FGI | 24
W74 | Maximum effective current value | ✔ | ✔ | W | 74 | 5F10 | 4B | 104A | 0F4A | 3915 | RTU | 19
W74 | Maximum effective current value | ✔ | ✔ | W | 74 | 5F10 | 4B | 104A | 0F4A | 3915 | BUS | 24
W75 | Main circuit capacitor's capacitor | ✔ | ✔ | W | 75 | 5F10 | 4C | 104B | 0F4B | 3916 | All | 3
W78 | Number of startups | ✔ | ✔ | W | 78 | 5F10 | 4F | 104E | 0F4E | 3919 | All | 1
W81 | Integrating electric power | ✔ | ✔ | W | 81 | 5F10 | 52 | 1051 | 0F51 | 3922 | All | 93
W82 | Data used integrating electric power | ✔ | ✔ | W | 82 | 5F10 | 53 | 1052 | 0F52 | 3923 | All | 45
W83 | Number of RS485 ch1 errors | ✔ | ✔ | W | 83 | 5F10 | 54 | 1053 | 0F53 | 3924 | All | 1
W84 | Contents of RS485 ch1 error | ✔ | ✔ | W | 84 | 5F10 | 55 | 1054 | 0F54 | 3925 | All | 20
W85 | Number of RS485 ch2 errors | ✔ | ✔ | W | 85 | 5F10 | 56 | 1055 | 0F55 | 3926 | All | 1
W86 | Number of option communications errors | ✔ | ✔ | W | 86 | 5F10 | 57 | 1056 | 0F56 | 3927 | All | 1
W87 | Inverter's keypad's ROM version | ✔ | ✔ | W | 87 | 5F10 | 58 | 1057 | 0F57 | 3928 | All | 35
W89 | Remote keypad's ROM version | ✔ | ✔ | W | 89 | 5F10 | 5A | 1059 | 0F59 | 3930 | All | 35
W90 | Option 1 ROM version | ✔ | ✔ | W | 90 | 5F10 | 5B | 105A | 0F5A | 3931 | All | 35
W91 | Option 2 ROM version | ✔ | ✔ | W | 91 | 5F10 | 5C | 105B | 0F5B | 3932 | All | 35
W92 | Option 3 ROM version | ✔ | ✔ | W | 92 | 5F10 | 5D | 105C | 0F5C | 3933 | All | 35
W94 | Contents of RS485 ch2 error | ✔ | ✔ | W | 94 | 5F10 | 5F | 105E | 0F5E | 3935 | All | 20
W95 | Number of option communications errors | ✔ | ✔ | W | 95 | 5F10 | 60 | 105F | 0F5F | 3936 | All | 1
W96 | Option communicate error contents | ✔ | ✔ | W | 96 | 5F10 | 61 | 1060 | 0F60 | 3937 | All | 1
W97 | Option communicate error contents | ✔ | ✔ | W | 97 | 5F10 | 62 | 1061 | 0F61 | 3938 | All | 1
W98 | Number of option communications errors | ✔ | ✔ | W | 98 | 5F10 | 63 | 1062 | 0F62 | 3939 | All | 1
W99 | Option communicate error contents | ✔ | ✔ | W | 99 | 5F10 | 64 | 1063 | 0F63 | 3940 | All | 1
W101 | Present date(Year/Month) | ✔ | ✔ | W1 | 01 | 5F17 | 02 | 1701 | 1601 | 5634 | All | 85
W102 | Present date(Day/Hour) | ✔ | ✔ | W1 | 02 | 5F17 | 03 | 1702 | 1602 | 5635 | All | 86
W103 | Present date(Minute/Second) | ✔ | ✔ | W1 | 03 | 5F17 | 04 | 1703 | 1603 | 5636 | All | 87
W105 | Output current (U) | ✔ | ✔ | W1 | 05 | 5F17 | 06 | 1705 | 1605 | 5638 | All | 24
W106 | Output current (V) | ✔ | ✔ | W1 | 06 | 5F17 | 07 | 1706 | 1606 | 5639 | All | 24
W107 | Output current (W) | ✔ | ✔ | W1 | 07 | 5F17 | 08 | 1707 | 1607 | 5640 | All | 24
W167 | Life of PC board electrolytic capacitor | ✔ | ✔ | W1 | 67 | 5F17 | 44 | 1743 | 1643 | 5700 | All | 74
W168 | Life of cooling fan | ✔ | ✔ | W1 | 68 | 5F17 | 45 | 1744 | 1644 | 5701 | All | 74
W170 | Cumulative operation time | ✔ | ✔ | W1 | 70 | 5F17 | 47 | 1746 | 1646 | 5703 | All | 74
W181 | Integrating electric power | ✔ | ✔ | W1 | 81 | 5F17 | 52 | 1751 | 1651 | 5714 | All | 24
W202 | PID command 1 (physical quantity) | ✔ | ✔ | W2 | 02 | 5F18 | 03 | 1802 | 1702 | 5891 | All | 12
W203 | PID feedback 1 (physical quantity) | ✔ | ✔ | W2 | 03 | 5F18 | 04 | 1803 | 1703 | 5892 | All | 12
W205 | PID command 2 (physical quantity) | ✔ | ✔ | W2 | 05 | 5F18 | 06 | 1805 | 1705 | 5894 | All | 12
W206 | PID feedback 2 (physical quantity) | ✔ | ✔ | W2 | 06 | 5F18 | 07 | 1806 | 1706 | 5895 | All | 12
W212 | External PID 1 final command (physical quantity) | ✔ | ✔ | W2 | 12 | 5F18 | 0D | 180C | 170C | 5901 | All | 12
W213 | External PID 1 final feedback (physical quantity) | ✔ | ✔ | W2 | 13 | 5F18 | 0E | 180D | 170D | 5902 | All | 12
W214 | External PID 1 command (physical quantity) | ✔ | ✔ | W2 | 14 | 5F18 | 0F | 180E | 170E | 5903 | All | 12
W215 | External PID 1 feedback (physical quantity) | ✔ | ✔ | W2 | 15 | 5F18 | 10 | 180F | 170F | 5904 | All | 12
W217 | External PID 1manual command (%) | ✔ | ✔ | W2 | 17 | 5F18 | 12 | 1811 | 1711 | 5906 | All | 6
W218 | External PID 1 final output (%) | ✔ | ✔ | W2 | 18 | 5F18 | 13 | 1812 | 1712 | 5907 | All | 4
W224 | External PID 2 command (physical quantity) | ✔ | ✔ | W2 | 24 | 5F18 | 19 | 1818 | 1718 | 5913 | All | 12
W225 | External PID 2 feedback (physical quantity) | ✔ | ✔ | W2 | 25 | 5F18 | 1A | 1819 | 1719 | 5914 | All | 12
W227 | External PID 2 manual command (%) | ✔ | ✔ | W2 | 27 | 5F18 | 1C | 181B | 171B | 5916 | All | 6
W228 | External PID 2 final output (%) | ✔ | ✔ | W2 | 28 | 5F18 | 1D | 181C | 171C | 5917 | All | 4
W234 | External PID 3 command (physical quantity) | ✔ | ✔ | W2 | 34 | 5F18 | 23 | 1822 | 1722 | 5923 | All | 12
W235 | External PID 3 feedback (physical quantity) | ✔ | ✔ | W2 | 35 | 5F18 | 24 | 1823 | 1723 | 5924 | All | 12
W237 | External PID 3 manual command (%) | ✔ | ✔ | W2 | 37 | 5F18 | 26 | 1825 | 1725 | 5926 | All | 6
W238 | External PID 3 final output (%) | ✔ | ✔ | W2 | 38 | 5F18 | 27 | 1826 | 1726 | 5927 | All | 4
W250 | Mutual operation Slave 1 output frequency (before slip compensation) | ✔ | x | W2 | 50 | 5F18 | 33 | 1832 | 1732 | 5939 | All | 22
W251 | Mutual operation Slave 1 output current | ✔ | x | W2 | 51 | 5F18 | 34 | 1833 | 1733 | 5940 | All | 24
W252 | Mutual operation Slave 1 input power | ✔ | x | W2 | 52 | 5F18 | 35 | 1834 | 1734 | 5941 | All | 24
W253 | Mutual operation Slave 1 alarm history (latest) | ✔ | x | W2 | 53 | 5F18 | 36 | 1835 | 1735 | 5942 | All | 10
W255 | Mutual operation Slave 2 output frequency before slip compensation | ✔ | x | W2 | 55 | 5F18 | 38 | 1837 | 1737 | 5944 | All | 22
W256 | Mutual operation Slave 2 output cuurent | ✔ | x | W2 | 56 | 5F18 | 39 | 1838 | 1738 | 5945 | All | 24
W257 | Mutual operation Slave 2 input power | ✔ | x | W2 | 57 | 5F18 | 3A | 1839 | 1739 | 5946 | All | 24
W258 | Mutual operation Slave 2 alarm history (latest) | ✔ | x | W2 | 58 | 5F18 | 3B | 183A | 173A | 5947 | All | 10
W301 | Integrating electric power monitor select | ✔ | ✔ | W3 | 01 | 5F19 | 02 | 1901 | 1801 | 6146 | All | 1
W302 | Integrating electric power start date(Day/Hour) | ✔ | ✔ | W3 | 02 | 5F19 | 03 | 1902 | 1802 | 6147 | All | 85
W303 | Integrating electric power start date(Minute/Second) | ✔ | ✔ | W3 | 03 | 5F19 | 04 | 1903 | 1803 | 6148 | All | 86
W304 | Integrating electric power monitor 1 | ✔ | ✔ | W3 | 04 | 5F19 | 05 | 1904 | 1804 | 6149 | All | 45
W305 | Integrating electric power monitor 2 | ✔ | ✔ | W3 | 05 | 5F19 | 06 | 1905 | 1805 | 6150 | All | 45
W306 | Integrating electric power monitor 3 | ✔ | ✔ | W3 | 06 | 5F19 | 07 | 1906 | 1806 | 6151 | All | 45
W307 | Integrating electric power monitor 4 | ✔ | ✔ | W3 | 07 | 5F19 | 08 | 1907 | 1807 | 6152 | All | 45
W308 | Integrating electric power monitor 5 | ✔ | ✔ | W3 | 08 | 5F19 | 09 | 1908 | 1808 | 6153 | All | 45
W309 | Integrating electric power monitor 6 | ✔ | ✔ | W3 | 09 | 5F19 | 0A | 1909 | 1809 | 6154 | All | 45
W310 | Integrating electric power monitor 7 | ✔ | ✔ | W3 | 10 | 5F19 | 0B | 190A | 180A | 6155 | All | 45
W311 | Integrating electric power monitor 8 | ✔ | ✔ | W3 | 11 | 5F19 | 0C | 190B | 180B | 6156 | All | 45
W312 | Integrating electric power monitor 9 | ✔ | ✔ | W3 | 12 | 5F19 | 0D | 190C | 180C | 6157 | All | 45
W313 | Integrating electric power monitor 10 | ✔ | ✔ | W3 | 13 | 5F19 | 0E | 190D | 180D | 6158 | All | 45
W314 | Integrating electric power monitor 11 | ✔ | ✔ | W3 | 14 | 5F19 | 0F | 190E | 180E | 6159 | All | 45
W315 | Integrating electric power monitor 12 | ✔ | ✔ | W3 | 15 | 5F19 | 10 | 190F | 180F | 6160 | All | 45
W316 | Integrating electric power monitor 13 | ✔ | ✔ | W3 | 16 | 5F19 | 11 | 1910 | 1810 | 6161 | All | 45
W317 | Integrating electric power monitor 14 | ✔ | ✔ | W3 | 17 | 5F19 | 12 | 1911 | 1811 | 6162 | All | 45
W318 | Integrating electric power monitor 15 | ✔ | ✔ | W3 | 18 | 5F19 | 13 | 1912 | 1812 | 6163 | All | 45
W319 | Integrating electric power monitor 16 | ✔ | ✔ | W3 | 19 | 5F19 | 14 | 1913 | 1813 | 6164 | All | 45
W320 | Integrating electric power monitor 17 | ✔ | ✔ | W3 | 20 | 5F19 | 15 | 1914 | 1814 | 6165 | All | 45
W321 | Integrating electric power monitor 18 | ✔ | ✔ | W3 | 21 | 5F19 | 16 | 1915 | 1815 | 6166 | All | 45
W322 | Integrating electric power monitor 19 | ✔ | ✔ | W3 | 22 | 5F19 | 17 | 1916 | 1816 | 6167 | All | 45
W323 | Integrating electric power monitor 20 | ✔ | ✔ | W3 | 23 | 5F19 | 18 | 1917 | 1817 | 6168 | All | 45
W324 | Integrating electric power monitor 21 | ✔ | ✔ | W3 | 24 | 5F19 | 19 | 1918 | 1818 | 6169 | All | 45
W325 | Integrating electric power monitor 22 | ✔ | ✔ | W3 | 25 | 5F19 | 1A | 1919 | 1819 | 6170 | All | 45
W326 | Integrating electric power monitor 23 | ✔ | ✔ | W3 | 26 | 5F19 | 1B | 191A | 181A | 6171 | All | 45
W327 | Integrating electric power monitor 24 | ✔ | ✔ | W3 | 27 | 5F19 | 1C | 191B | 181B | 6172 | All | 45
W328 | Integrating electric power monitor 25 | ✔ | ✔ | W3 | 28 | 5F19 | 1D | 191C | 181C | 6173 | All | 45
W329 | Integrating electric power monitor 26 | ✔ | ✔ | W3 | 29 | 5F19 | 1E | 191D | 181D | 6174 | All | 45
W330 | Integrating electric power monitor 27 | ✔ | ✔ | W3 | 30 | 5F19 | 1F | 191E | 181E | 6175 | All | 45
W331 | Integrating electric power monitor 28 | ✔ | ✔ | W3 | 31 | 5F19 | 20 | 191F | 181F | 6176 | All | 45
W332 | Integrating electric power monitor 29 | ✔ | ✔ | W3 | 32 | 5F19 | 21 | 1920 | 1820 | 6177 | All | 45
W333 | Integrating electric power monitor 30 | ✔ | ✔ | W3 | 33 | 5F19 | 22 | 1921 | 1821 | 6178 | All | 45
W334 | Integrating electric power monitor 31 | ✔ | ✔ | W3 | 34 | 5F19 | 23 | 1922 | 1822 | 6179 | All | 45
W335 | Integrating electric power monitor 32 | ✔ | ✔ | W3 | 35 | 5F19 | 24 | 1923 | 1823 | 6180 | All | 45
W336 | Integrating electric power monitor 33 | ✔ | ✔ | W3 | 36 | 5F19 | 25 | 1924 | 1824 | 6181 | All | 45
W337 | Integrating electric power monitor 34 | ✔ | ✔ | W3 | 37 | 5F19 | 26 | 1925 | 1825 | 6182 | All | 45
W338 | Integrating electric power monitor 35 | ✔ | ✔ | W3 | 38 | 5F19 | 27 | 1926 | 1826 | 6183 | All | 45
W339 | Integrating electric power monitor 36 | ✔ | ✔ | W3 | 39 | 5F19 | 28 | 1927 | 1827 | 6184 | All | 45
W340 | Integrating electric power monitor 37 | ✔ | ✔ | W3 | 40 | 5F19 | 29 | 1928 | 1828 | 6185 | All | 45
W341 | Integrating electric power monitor 38 | ✔ | ✔ | W3 | 41 | 5F19 | 2A | 1929 | 1829 | 6186 | All | 45
W342 | Integrating electric power monitor 39 | ✔ | ✔ | W3 | 42 | 5F19 | 2B | 192A | 182A | 6187 | All | 45
W343 | Integrating electric power monitor 40 | ✔ | ✔ | W3 | 43 | 5F19 | 2C | 192B | 182B | 6188 | All | 45
W344 | Integrating electric power monitor 41 | ✔ | ✔ | W3 | 44 | 5F19 | 2D | 192C | 182C | 6189 | All | 45
W345 | Integrating electric power monitor 42 | ✔ | ✔ | W3 | 45 | 5F19 | 2E | 192D | 182D | 6190 | All | 45
W346 | Integrating electric power monitor 43 | ✔ | ✔ | W3 | 46 | 5F19 | 2F | 192E | 182E | 6191 | All | 45
W347 | Integrating electric power monitor 44 | ✔ | ✔ | W3 | 47 | 5F19 | 30 | 192F | 182F | 6192 | All | 45
W348 | Integrating electric power monitor 45 | ✔ | ✔ | W3 | 48 | 5F19 | 31 | 1930 | 1830 | 6193 | All | 45
W349 | Integrating electric power monitor 46 | ✔ | ✔ | W3 | 49 | 5F19 | 32 | 1931 | 1831 | 6194 | All | 45
W350 | Integrating electric power monitor 47 | ✔ | ✔ | W3 | 50 | 5F19 | 33 | 1932 | 1832 | 6195 | All | 45
W351 | Integrating electric power monitor 48 | ✔ | ✔ | W3 | 51 | 5F19 | 34 | 1933 | 1833 | 6196 | All | 45
W352 | Cumulative operation time 1 | ✔ | ✔ | W3 | 52 | 5F19 | 35 | 1934 | 1834 | 6197 | All | 45
W353 | Cumulative operation time 2 | ✔ | ✔ | W3 | 53 | 5F19 | 36 | 1935 | 1835 | 6198 | All | 45
W354 | Cumulative operation time 3 | ✔ | ✔ | W3 | 54 | 5F19 | 37 | 1936 | 1836 | 6199 | All | 45
W355 | Cumulative operation time 4 | ✔ | ✔ | W3 | 55 | 5F19 | 38 | 1937 | 1837 | 6200 | All | 45
W356 | Cumulative operation time 5 | ✔ | ✔ | W3 | 56 | 5F19 | 39 | 1938 | 1838 | 6201 | All | 45
W357 | Cumulative operation time 6 | ✔ | ✔ | W3 | 57 | 5F19 | 3A | 1939 | 1839 | 6202 | All | 45
W358 | Cumulative operation time 7 | ✔ | ✔ | W3 | 58 | 5F19 | 3B | 193A | 183A | 6203 | All | 45
W359 | Cumulative operation time 8 | ✔ | ✔ | W3 | 59 | 5F19 | 3C | 193B | 183B | 6204 | All | 45
W360 | Cumulative operation time 9 | ✔ | ✔ | W3 | 60 | 5F19 | 3D | 193C | 183C | 6205 | All | 45
W361 | Cumulative operation time 10 | ✔ | ✔ | W3 | 61 | 5F19 | 3E | 193D | 183D | 6206 | All | 45
W362 | Cumulative operation time 11 | ✔ | ✔ | W3 | 62 | 5F19 | 3F | 193E | 183E | 6207 | All | 45
W363 | Cumulative operation time 12 | ✔ | ✔ | W3 | 63 | 5F19 | 40 | 193F | 183F | 6208 | All | 45
W364 | Cumulative operation time 13 | ✔ | ✔ | W3 | 64 | 5F19 | 41 | 1940 | 1840 | 6209 | All | 45
W365 | Cumulative operation time 14 | ✔ | ✔ | W3 | 65 | 5F19 | 42 | 1941 | 1841 | 6210 | All | 45
W366 | Cumulative operation time 15 | ✔ | ✔ | W3 | 66 | 5F19 | 43 | 1942 | 1842 | 6211 | All | 45
W367 | Cumulative operation time 16 | ✔ | ✔ | W3 | 67 | 5F19 | 44 | 1943 | 1843 | 6212 | All | 45
W368 | Cumulative operation time 17 | ✔ | ✔ | W3 | 68 | 5F19 | 45 | 1944 | 1844 | 6213 | All | 45
W369 | Cumulative operation time 18 | ✔ | ✔ | W3 | 69 | 5F19 | 46 | 1945 | 1845 | 6214 | All | 45
W370 | Cumulative operation time 19 | ✔ | ✔ | W3 | 70 | 5F19 | 47 | 1946 | 1846 | 6215 | All | 45
W371 | Cumulative operation time 20 | ✔ | ✔ | W3 | 71 | 5F19 | 48 | 1947 | 1847 | 6216 | All | 45
W372 | Cumulative operation time 21 | ✔ | ✔ | W3 | 72 | 5F19 | 49 | 1948 | 1848 | 6217 | All | 45
W373 | Cumulative operation time 22 | ✔ | ✔ | W3 | 73 | 5F19 | 4A | 1949 | 1849 | 6218 | All | 45
W374 | Cumulative operation time 23 | ✔ | ✔ | W3 | 74 | 5F19 | 4B | 194A | 184A | 6219 | All | 45
W375 | Cumulative operation time 24 | ✔ | ✔ | W3 | 75 | 5F19 | 4C | 194B | 184B | 6220 | All | 45
W376 | Cumulative operation time 25 | ✔ | ✔ | W3 | 76 | 5F19 | 4D | 194C | 184C | 6221 | All | 45
W377 | Cumulative operation time 26 | ✔ | ✔ | W3 | 77 | 5F19 | 4E | 194D | 184D | 6222 | All | 45
W378 | Cumulative operation time 27 | ✔ | ✔ | W3 | 78 | 5F19 | 4F | 194E | 184E | 6223 | All | 45
W379 | Cumulative operation time 28 | ✔ | ✔ | W3 | 79 | 5F19 | 50 | 194F | 184F | 6224 | All | 45
W380 | Cumulative operation time 29 | ✔ | ✔ | W3 | 80 | 5F19 | 51 | 1950 | 1850 | 6225 | All | 45
W381 | Cumulative operation time 30 | ✔ | ✔ | W3 | 81 | 5F19 | 52 | 1951 | 1851 | 6226 | All | 45
W382 | Cumulative operation time 31 | ✔ | ✔ | W3 | 82 | 5F19 | 53 | 1952 | 1852 | 6227 | All | 45
W383 | Cumulative operation time 32 | ✔ | ✔ | W3 | 83 | 5F19 | 54 | 1953 | 1853 | 6228 | All | 45
W384 | Cumulative operation time 33 | ✔ | ✔ | W3 | 84 | 5F19 | 55 | 1954 | 1854 | 6229 | All | 45
W385 | Cumulative operation time 34 | ✔ | ✔ | W3 | 85 | 5F19 | 56 | 1955 | 1855 | 6230 | All | 45
W386 | Cumulative operation time 35 | ✔ | ✔ | W3 | 86 | 5F19 | 57 | 1956 | 1856 | 6231 | All | 45
W387 | Cumulative operation time 36 | ✔ | ✔ | W3 | 87 | 5F19 | 58 | 1957 | 1857 | 6232 | All | 45
W388 | Cumulative operation time 37 | ✔ | ✔ | W3 | 88 | 5F19 | 59 | 1958 | 1858 | 6233 | All | 45
W389 | Cumulative operation time 38 | ✔ | ✔ | W3 | 89 | 5F19 | 5A | 1959 | 1859 | 6234 | All | 45
W390 | Cumulative operation time 39 | ✔ | ✔ | W3 | 90 | 5F19 | 5B | 195A | 185A | 6235 | All | 45
W391 | Cumulative operation time 40 | ✔ | ✔ | W3 | 91 | 5F19 | 5C | 195B | 185B | 6236 | All | 45
W392 | Cumulative operation time 41 | ✔ | ✔ | W3 | 92 | 5F19 | 5D | 195C | 185C | 6237 | All | 45
W393 | Cumulative operation time 42 | ✔ | ✔ | W3 | 93 | 5F19 | 5E | 195D | 185D | 6238 | All | 45
W394 | Cumulative operation time 43 | ✔ | ✔ | W3 | 94 | 5F19 | 5F | 195E | 185E | 6239 | All | 45
W395 | Cumulative operation time 44 | ✔ | ✔ | W3 | 95 | 5F19 | 60 | 195F | 185F | 6240 | All | 45
W396 | Cumulative operation time 45 | ✔ | ✔ | W3 | 96 | 5F19 | 61 | 1960 | 1860 | 6241 | All | 45
W397 | Cumulative operation time 46 | ✔ | ✔ | W3 | 97 | 5F19 | 62 | 1961 | 1861 | 6242 | All | 45
W398 | Cumulative operation time 47 | ✔ | ✔ | W3 | 98 | 5F19 | 63 | 1962 | 1862 | 6243 | All | 45
W399 | Cumulative operation time 48 | ✔ | ✔ | W3 | 99 | 5F19 | 64 | 1963 | 1863 | 6244 | All | 45
X00 | Alarm history (latest) | ✔ | ✔ | X | 00 | 5F11 | 01 | 1100 | 1000 | 4097 | All | 41
X01 | Multiple alarm1 (latest) | ✔ | ✔ | X | 01 | 5F11 | 02 | 1101 | 1001 | 4098 | All | 40
X02 | Multiple alarm2 (latest) | ✔ | ✔ | X | 02 | 5F11 | 03 | 1102 | 1002 | 4099 | All | 40
X03 | Sub code (latest) | ✔ | ✔ | X | 03 | 5F11 | 04 | 1103 | 1003 | 4100 | All | 1
X04 | Multiple alarm1 sub code (latest) | ✔ | ✔ | X | 04 | 5F11 | 05 | 1104 | 1004 | 4101 | All | 1
X05 | Alarm history (last) | ✔ | ✔ | X | 05 | 5F11 | 06 | 1105 | 1005 | 4102 | All | 41
X06 | Multiple alarm1 (last) | ✔ | ✔ | X | 06 | 5F11 | 07 | 1106 | 1006 | 4103 | All | 40
X07 | Multiple alarm2 (last) | ✔ | ✔ | X | 07 | 5F11 | 08 | 1107 | 1007 | 4104 | All | 40
X08 | Sub code (last) | ✔ | ✔ | X | 08 | 5F11 | 09 | 1108 | 1008 | 4105 | All | 1
X09 | Multiple alarm1 sub code (last) | ✔ | ✔ | X | 09 | 5F11 | 0A | 1109 | 1009 | 4106 | All | 1
X10 | Alarm history (second last) | ✔ | ✔ | X | 10 | 5F11 | 0B | 110A | 100A | 4107 | All | 41
X11 | Multiple alarm1 (second last) | ✔ | ✔ | X | 11 | 5F11 | 0C | 110B | 100B | 4108 | All | 40
X12 | Multiple alarm2 (second last) | ✔ | ✔ | X | 12 | 5F11 | 0D | 110C | 100C | 4109 | All | 40
X13 | Sub code (second last) | ✔ | ✔ | X | 13 | 5F11 | 0E | 110D | 100D | 4110 | All | 1
X14 | Multiple alarm1 sub code (second last) | ✔ | ✔ | X | 14 | 5F11 | 0F | 110E | 100E | 4111 | All | 1
X15 | Alarm history (third last) | ✔ | ✔ | X | 15 | 5F11 | 10 | 110F | 100F | 4112 | All | 41
X16 | Multiple alarm1 (third last) | ✔ | ✔ | X | 16 | 5F11 | 11 | 1110 | 1010 | 4113 | All | 40
X17 | Multiple alarm2 (third last) | ✔ | ✔ | X | 17 | 5F11 | 12 | 1111 | 1011 | 4114 | All | 40
X18 | Sub code (third last) | ✔ | ✔ | X | 18 | 5F11 | 13 | 1112 | 1012 | 4115 | All | 1
X19 | Multiple alarm1 sub code (third last) | ✔ | ✔ | X | 19 | 5F11 | 14 | 1113 | 1013 | 4116 | All | 1
X20 | Latest info. on alarm (output frequency) | ✔ | ✔ | X | 20 | 5F11 | 15 | 1114 | 1014 | 4117 | All | 22
X21 | Latest info. on alarm (output current) | ✔ | ✔ | X | 21 | 5F11 | 16 | 1115 | 1015 | 4118 | FGI | 24
X21 | Latest info. on alarm (output current) | ✔ | ✔ | X | 21 | 5F11 | 16 | 1115 | 1015 | 4118 | RTU | 19
X21 | Latest info. on alarm (output current) | ✔ | ✔ | X | 21 | 5F11 | 16 | 1115 | 1015 | 4118 | BUS | 24
X22 | Latest info. on alarm (output voltage) | ✔ | ✔ | X | 22 | 5F11 | 17 | 1116 | 1016 | 4119 | All | 1
X23 | Latest info. on alarm (Torque) | ✔ | ✔ | X | 23 | 5F11 | 18 | 1117 | 1017 | 4120 | All | 2
X24 | Latest info. on alarm (set frequency) | ✔ | ✔ | X | 24 | 5F11 | 19 | 1118 | 1018 | 4121 | All | 22
X25 | Latest info. on alarm (running status) | ✔ | ✔ | X | 25 | 5F11 | 1A | 1119 | 1019 | 4122 | All | 16
X26 | Latest info. on alarm (cumulative ope. time) | ✔ | ✔ | X | 26 | 5F11 | 1B | 111A | 101A | 4123 | All | 1
X27 | Latest info. on alarm (number of startups) | ✔ | ✔ | X | 27 | 5F11 | 1C | 111B | 101B | 4124 | All | 1
X28 | Latest info. on alarm (DC link circuit voltage) | ✔ | ✔ | X | 28 | 5F11 | 1D | 111C | 101C | 4125 | All | 1
X29 | Latest info. on alarm (Internal air temperature) | ✔ | ✔ | X | 29 | 5F11 | 1E | 111D | 101D | 4126 | All | 1
X30 | Latest info. on alarm (heat sink temperature) | ✔ | ✔ | X | 30 | 5F11 | 1F | 111E | 101E | 4127 | All | 1
X31 | Latest info. on alarm (input terminal) | ✔ | ✔ | X | 31 | 5F11 | 20 | 111F | 101F | 4128 | All | 43
X32 | Latest info. on alarm (output terminal) | ✔ | ✔ | X | 32 | 5F11 | 21 | 1120 | 1020 | 4129 | All | 15
X33 | Latest info. on alarm (input terminal(com.)) | ✔ | ✔ | X | 33 | 5F11 | 22 | 1121 | 1021 | 4130 | All | 14
X34 | Latest info. on alarm (output terminal(com.)) | ✔ | ✔ | X | 34 | 5F11 | 23 | 1122 | 1022 | 4131 | All | 15
X35 | Latest info. on alarm (input power) | ✔ | ✔ | X | 35 | 5F11 | 24 | 1123 | 1023 | 4132 | All | 24
X36 | Latest info. on alarm (Operation status 2) | ✔ | ✔ | X | 36 | 5F11 | 25 | 1124 | 1024 | 4133 | All | 76
X37 | Latest info. on alarm (speed detection) | ✔ | ✔ | X | 37 | 5F11 | 26 | 1125 | 1025 | 4134 | All | 29
X38 | Latest info. on alarm (Operation status 3) | ✔ | ✔ | X | 38 | 5F11 | 27 | 1126 | 1026 | 4135 | All | 44
X54 | Light alarm contents (4th last) | ✔ | ✔ | X | 54 | 5F11 | 37 | 1136 | 1036 | 4151 | All | 41
X55 | Light alarm contents (5th last) | ✔ | ✔ | X | 55 | 5F11 | 38 | 1137 | 1037 | 4152 | All | 41
X60 | Last info. on alarm (output frequency) | ✔ | ✔ | X | 60 | 5F11 | 3D | 113C | 103C | 4157 | All | 22
X61 | Last info. on alarm (output current) | ✔ | ✔ | X | 61 | 5F11 | 3E | 113D | 103D | 4158 | FGI | 24
X61 | Last info. on alarm (output current) | ✔ | ✔ | X | 61 | 5F11 | 3E | 113D | 103D | 4158 | RTU | 19
X61 | Last info. on alarm (output current) | ✔ | ✔ | X | 61 | 5F11 | 3E | 113D | 103D | 4158 | BUS | 24
X62 | Last info. on alarm (output voltage) | ✔ | ✔ | X | 62 | 5F11 | 3F | 113E | 103E | 4159 | All | 1
X63 | Last info. on alarm (Torque) | ✔ | ✔ | X | 63 | 5F11 | 40 | 113F | 103F | 4160 | All | 2
X64 | Last info. on alarm (set frequency) | ✔ | ✔ | X | 64 | 5F11 | 41 | 1140 | 1040 | 4161 | All | 22
X65 | Last info. on alarm (operation status) | ✔ | ✔ | X | 65 | 5F11 | 42 | 1141 | 1041 | 4162 | All | 16
X66 | Last info. on alarm (cumulative ope. time) | ✔ | ✔ | X | 66 | 5F11 | 43 | 1142 | 1042 | 4163 | All | 1
X67 | Last info. on alarm (number of startups) | ✔ | ✔ | X | 67 | 5F11 | 44 | 1143 | 1043 | 4164 | All | 1
X68 | Last info. on alarm (DC link circuit voltage) | ✔ | ✔ | X | 68 | 5F11 | 45 | 1144 | 1044 | 4165 | All | 1
X69 | Last info. on alarm (Internal air temperature) | ✔ | ✔ | X | 69 | 5F11 | 46 | 1145 | 1045 | 4166 | All | 1
X70 | Last info. on alarm (heat sink temperature) | ✔ | ✔ | X | 70 | 5F11 | 47 | 1146 | 1046 | 4167 | All | 1
X71 | Last info. on alarm (input terminal) | ✔ | ✔ | X | 71 | 5F11 | 48 | 1147 | 1047 | 4168 | All | 43
X72 | Last info. on alarm (output terminal) | ✔ | ✔ | X | 72 | 5F11 | 49 | 1148 | 1048 | 4169 | All | 15
X73 | Last info. on alarm (input terminal(com.)) | ✔ | ✔ | X | 73 | 5F11 | 4A | 1149 | 1049 | 4170 | All | 14
X74 | Last info. on alarm (output terminal(com.)) | ✔ | ✔ | X | 74 | 5F11 | 4B | 114A | 104A | 4171 | All | 15
X76 | Last info. on alarm (Operation status 2) | ✔ | ✔ | X | 76 | 5F11 | 4D | 114C | 104C | 4173 | All | 76
X77 | Last info. on alarm (Speed detection) | ✔ | ✔ | X | 77 | 5F11 | 4E | 114D | 104D | 4174 | All | 29
X78 | Last info. on alarm (Operation status 3) | ✔ | ✔ | X | 78 | 5F11 | 4F | 114E | 104E | 4175 | All | 44
X89 | Customizable Logic (Digital input output) | ✔ | ✔ | X | 89 | 5F11 | 5A | 1159 | 1059 | 4186 | All | 95
X90 | Customizable Logic (Timer) | ✔ | ✔ | X | 90 | 5F11 | 5B | 115A | 105A | 4187 | All | 5
X91 | Customizable Logic (Analog input 1) | ✔ | ✔ | X | 91 | 5F11 | 5C | 115B | 105B | 4188 | All | 12
X92 | Customizable Logic (Analog input 2) | ✔ | ✔ | X | 92 | 5F11 | 5D | 115C | 105C | 4189 | All | 12
X93 | Customizable Logic (Analog output) | ✔ | ✔ | X | 93 | 5F11 | 5E | 115D | 105D | 4190 | All | 12
X94 | Relay output terminal | ✔ | ✔ | X | 94 | 5F11 | 5F | 115E | 105E | 4191 | All | 91
X95 | Flow Sensor Monitor | ✔ | x | X | 95 | 5F11 | 60 | 115F | 105F | 4192 | All | 12
X96 | Terminal [CS2] output current | ✔ | ✔ | X | 96 | 5F11 | 61 | 1160 | 1060 | 4193 | All | 3
X97 | Terminal [PTC] input voltage | ✔ | ✔ | X | 97 | 5F11 | 62 | 1161 | 1061 | 4194 | All | 4
X98 | Pt Channel 1 temperature | ✔ | ✔ | X | 98 | 5F11 | 63 | 1162 | 1062 | 4195 | All | 6
X99 | Pt Channel 2 temperature | ✔ | ✔ | X | 99 | 5F11 | 64 | 1163 | 1063 | 4196 | All | 6
X105 | Latest alarm generation date(Year/Month) | ✔ | ✔ | X1 | 05 | 5F1A | 06 | 1A05 | 1905 | 6406 | All | 85
X106 | Latest alarm generation date(Day/Hour) | ✔ | ✔ | X1 | 06 | 5F1A | 07 | 1A06 | 1906 | 6407 | All | 86
X107 | Latest alarm generation date(Minute/Second) | ✔ | ✔ | X1 | 07 | 5F1A | 08 | 1A07 | 1907 | 6408 | All | 87
X115 | Last alarm generation date(Year/Month) | ✔ | ✔ | X1 | 15 | 5F1A | 10 | 1A0F | 190F | 6416 | All | 85
X116 | Last alarm generation date(Day/Hour) | ✔ | ✔ | X1 | 16 | 5F1A | 11 | 1A10 | 1910 | 6417 | All | 86
X117 | Last alarm generation date(Minute/Second) | ✔ | ✔ | X1 | 17 | 5F1A | 12 | 1A11 | 1911 | 6418 | All | 87
X125 | 2nd last alarm generation date(Year/Month) | ✔ | ✔ | X1 | 25 | 5F1A | 1A | 1A19 | 1919 | 6426 | All | 85
X126 | 2nd last alarm generation date(Day/Hour) | ✔ | ✔ | X1 | 26 | 5F1A | 1B | 1A1A | 191A | 6427 | All | 86
X127 | 2nd last alarm generation date(Minute/Second) | ✔ | ✔ | X1 | 27 | 5F1A | 1C | 1A1B | 191B | 6428 | All | 87
X135 | 3rd last alarm generation date(Year/Month) | ✔ | ✔ | X1 | 35 | 5F1A | 24 | 1A23 | 1923 | 6436 | All | 85
X136 | 3rd last alarm generation date(Day/Hour) | ✔ | ✔ | X1 | 36 | 5F1A | 25 | 1A24 | 1924 | 6437 | All | 86
X137 | 3rd last alarm generation date(Minute/Second) | ✔ | ✔ | X1 | 37 | 5F1A | 26 | 1A25 | 1925 | 6438 | All | 87
X140 | Alarm history (4th last) | ✔ | ✔ | X1 | 40 | 5F1A | 29 | 1A28 | 1928 | 6441 | All | 41
X145 | 4th last alarm generation date(Year/Month) | ✔ | ✔ | X1 | 45 | 5F1A | 2E | 1A2D | 192D | 6446 | All | 85
X146 | 4th last alarm generation date(Day/Hour) | ✔ | ✔ | X1 | 46 | 5F1A | 2F | 1A2E | 192E | 6447 | All | 86
X147 | 4th last alarm generation date(Minute/Second) | ✔ | ✔ | X1 | 47 | 5F1A | 30 | 1A2F | 192F | 6448 | All | 87
X150 | Alarm history (5th last) | ✔ | ✔ | X1 | 50 | 5F1A | 33 | 1A32 | 1932 | 6451 | All | 41
X155 | 5th last alarm generation date(Year/Month) | ✔ | ✔ | X1 | 55 | 5F1A | 38 | 1A37 | 1937 | 6456 | All | 85
X156 | 5th last alarm generation date(Day/Hour) | ✔ | ✔ | X1 | 56 | 5F1A | 39 | 1A38 | 1938 | 6457 | All | 86
X157 | 5th last alarm generation date(Minute/Second) | ✔ | ✔ | X1 | 57 | 5F1A | 3A | 1A39 | 1939 | 6458 | All | 87
X160 | Alarm history (6th last) | ✔ | ✔ | X1 | 60 | 5F1A | 3D | 1A3C | 193C | 6461 | All | 41
X165 | 6th last alarm generation date(Year/Month) | ✔ | ✔ | X1 | 65 | 5F1A | 42 | 1A41 | 1941 | 6466 | All | 85
X166 | 6th last alarm generation date(Day/Hour) | ✔ | ✔ | X1 | 66 | 5F1A | 43 | 1A42 | 1942 | 6467 | All | 86
X167 | 6th last alarm generation date(Minute/Second) | ✔ | ✔ | X1 | 67 | 5F1A | 44 | 1A43 | 1943 | 6468 | All | 87
X170 | Alarm history (7th last) | ✔ | ✔ | X1 | 70 | 5F1A | 47 | 1A46 | 1946 | 6471 | All | 41
X175 | 7th last alarm generation date(Year/Month) | ✔ | ✔ | X1 | 75 | 5F1A | 4C | 1A4B | 194B | 6476 | All | 85
X176 | 7th last alarm generation date(Day/Hour) | ✔ | ✔ | X1 | 76 | 5F1A | 4D | 1A4C | 194C | 6477 | All | 86
X177 | 7th last alarm generation date(Minute/Second) | ✔ | ✔ | X1 | 77 | 5F1A | 4E | 1A4D | 194D | 6478 | All | 87
X180 | Alarm history (8th last) | ✔ | ✔ | X1 | 80 | 5F1A | 51 | 1A50 | 1950 | 6481 | All | 41
X185 | 8th last alarm generation date(Year/Month) | ✔ | ✔ | X1 | 85 | 5F1A | 56 | 1A55 | 1955 | 6486 | All | 85
X186 | 8th last alarm generation date(Day/Hour) | ✔ | ✔ | X1 | 86 | 5F1A | 57 | 1A56 | 1956 | 6487 | All | 86
X187 | 8th last alarm generation date(Minute/Second) | ✔ | ✔ | X1 | 87 | 5F1A | 58 | 1A57 | 1957 | 6488 | All | 87
X190 | Alarm history (9th last) | ✔ | ✔ | X1 | 90 | 5F1A | 5B | 1A5A | 195A | 6491 | All | 41
X195 | 9th last alarm generation date(Year/Month) | ✔ | ✔ | X1 | 95 | 5F1A | 60 | 1A5F | 195F | 6496 | All | 85
X196 | 9th last alarm generation date(Day/Hour) | ✔ | ✔ | X1 | 96 | 5F1A | 61 | 1A60 | 1960 | 6497 | All | 86
X197 | 9th last alarm generation date(Minute/Second) | ✔ | ✔ | X1 | 97 | 5F1A | 62 | 1A61 | 1961 | 6498 | All | 87
Z00 | Second last info. on alarm (output frequency) | ✔ | ✔ | Z | 00 | 5F12 | 01 | 1200 | 1100 | 4353 | All | 22
Z01 | Second last info. on alarm (output current) | ✔ | ✔ | Z | 01 | 5F12 | 02 | 1201 | 1101 | 4354 | FGI | 24
Z01 | Second last info. on alarm (output current) | ✔ | ✔ | Z | 01 | 5F12 | 02 | 1201 | 1101 | 4354 | RTU | 19
Z01 | Second last info. on alarm (output current) | ✔ | ✔ | Z | 01 | 5F12 | 02 | 1201 | 1101 | 4354 | BUS | 24
Z02 | Second last info. on alarm (output voltage) | ✔ | ✔ | Z | 02 | 5F12 | 03 | 1202 | 1102 | 4355 | All | 1
Z03 | Second last info. on alarm (Torque) | ✔ | ✔ | Z | 03 | 5F12 | 04 | 1203 | 1103 | 4356 | All | 2
Z04 | Second last info. on alarm (set frequency) | ✔ | ✔ | Z | 04 | 5F12 | 05 | 1204 | 1104 | 4357 | All | 22
Z05 | Second last info. on alarm (operation status) | ✔ | ✔ | Z | 05 | 5F12 | 06 | 1205 | 1105 | 4358 | All | 16
Z06 | Second last info. on alarm (cumulative ope. time) | ✔ | ✔ | Z | 06 | 5F12 | 07 | 1206 | 1106 | 4359 | All | 1
Z07 | Second last info. on alarm (number of startups) | ✔ | ✔ | Z | 07 | 5F12 | 08 | 1207 | 1107 | 4360 | All | 1
Z08 | Second last info. on alarm (DC link circuit voltage) | ✔ | ✔ | Z | 08 | 5F12 | 09 | 1208 | 1108 | 4361 | All | 1
Z09 | Second last info. on alarm (Internal air temperature) | ✔ | ✔ | Z | 09 | 5F12 | 0A | 1209 | 1109 | 4362 | All | 1
Z10 | Second last info. on alarm (heat sink temperature) | ✔ | ✔ | Z | 10 | 5F12 | 0B | 120A | 110A | 4363 | All | 1
Z11 | Second last info. on alarm (input terminal) | ✔ | ✔ | Z | 11 | 5F12 | 0C | 120B | 110B | 4364 | All | 43
Z12 | Second last info. on alarm (output terminal) | ✔ | ✔ | Z | 12 | 5F12 | 0D | 120C | 110C | 4365 | All | 15
Z13 | Second last info. on alarm (input terminal(com.)) | ✔ | ✔ | Z | 13 | 5F12 | 0E | 120D | 110D | 4366 | All | 14
Z14 | Second last info. on alarm (output terminal(com.)) | ✔ | ✔ | Z | 14 | 5F12 | 0F | 120E | 110E | 4367 | All | 15
Z16 | Second last info. on alarm (operation status 2) | ✔ | ✔ | Z | 16 | 5F12 | 11 | 1210 | 1110 | 4369 | All | 76
Z17 | Second last info. on alarm (Speed detection) | ✔ | ✔ | Z | 17 | 5F12 | 12 | 1211 | 1111 | 4370 | All | 29
Z18 | Second last info. on alarm (operation status 3) | ✔ | ✔ | Z | 18 | 5F12 | 13 | 1212 | 1112 | 4371 | All | 44
Z40 | Comulative operation time of motor (M1) | ✔ | ✔ | Z | 40 | 5F12 | 29 | 1228 | 1128 | 4393 | All | 74
Z48 | Retry history (latest) | ✔ | ✔ | Z | 48 | 5F12 | 31 | 1230 | 1130 | 4401 | All | 41
Z49 | Retry history (last) | ✔ | ✔ | Z | 49 | 5F12 | 32 | 1231 | 1131 | 4402 | All | 41
Z50 | Third last info. on alarm (output frequency) | ✔ | ✔ | Z | 50 | 5F12 | 33 | 1232 | 1132 | 4403 | All | 22
Z51 | Third last info. on alarm (output current) | ✔ | ✔ | Z | 51 | 5F12 | 34 | 1233 | 1133 | 4404 | FGI | 24
Z51 | Third last info. on alarm (output current) | ✔ | ✔ | Z | 51 | 5F12 | 34 | 1233 | 1133 | 4404 | RTU | 19
Z51 | Third last info. on alarm (output current) | ✔ | ✔ | Z | 51 | 5F12 | 34 | 1233 | 1133 | 4404 | BUS | 24
Z52 | Third last info. on alarm (output voltage) | ✔ | ✔ | Z | 52 | 5F12 | 35 | 1234 | 1134 | 4405 | All | 1
Z53 | Third last info. on alarm (Torque) | ✔ | ✔ | Z | 53 | 5F12 | 36 | 1235 | 1135 | 4406 | All | 2
Z54 | Third last info. on alarm (set frequency) | ✔ | ✔ | Z | 54 | 5F12 | 37 | 1236 | 1136 | 4407 | All | 22
Z55 | Third last info. on alarm (operation status) | ✔ | ✔ | Z | 55 | 5F12 | 38 | 1237 | 1137 | 4408 | All | 16
Z56 | Third last info. on alarm (cumulative ope. time) | ✔ | ✔ | Z | 56 | 5F12 | 39 | 1238 | 1138 | 4409 | All | 1
Z57 | Third last info. on alarm (number of startups) | ✔ | ✔ | Z | 57 | 5F12 | 3A | 1239 | 1139 | 4410 | All | 1
Z58 | Third last info. on alarm (DC link circuit voltage) | ✔ | ✔ | Z | 58 | 5F12 | 3B | 123A | 113A | 4411 | All | 1
Z59 | Third last info. on alarm (Internal air temperature) | ✔ | ✔ | Z | 59 | 5F12 | 3C | 123B | 113B | 4412 | All | 1
Z60 | Third last info. on alarm (heat sink temperature) | ✔ | ✔ | Z | 60 | 5F12 | 3D | 123C | 113C | 4413 | All | 1
Z61 | Third last info. on alarm (input terminal) | ✔ | ✔ | Z | 61 | 5F12 | 3E | 123D | 113D | 4414 | All | 43
Z62 | Third last info. on alarm (output terminal) | ✔ | ✔ | Z | 62 | 5F12 | 3F | 123E | 113E | 4415 | All | 15
Z63 | Third last info. on alarm (input terminal(com.)) | ✔ | ✔ | Z | 63 | 5F12 | 40 | 123F | 113F | 4416 | All | 14
Z64 | Third last info. on alarm (output terminal(com.)) | ✔ | ✔ | Z | 64 | 5F12 | 41 | 1240 | 1140 | 4417 | All | 15
Z66 | Third last info. on alarm (operation status 2) | ✔ | ✔ | Z | 66 | 5F12 | 43 | 1242 | 1142 | 4419 | All | 76
Z67 | Third last info. on alarm (Speed detection) | ✔ | ✔ | Z | 67 | 5F12 | 44 | 1243 | 1143 | 4420 | All | 29
Z68 | Third last info. on alarm (operation status 3) | ✔ | ✔ | Z | 68 | 5F12 | 45 | 1244 | 1144 | 4421 | All | 44
Z80 | Speed detection | ✔ | ✔ | Z | 80 | 5F12 | 51 | 1250 | 1150 | 4433 | All | 2
Z81 | Torque | ✔ | ✔ | Z | 81 | 5F12 | 52 | 1251 | 1151 | 4434 | All | 6
Z82 | Load rate | ✔ | ✔ | Z | 82 | 5F12 | 53 | 1252 | 1152 | 4435 | All | 6
Z83 | Motor output | ✔ | ✔ | Z | 83 | 5F12 | 54 | 1253 | 1153 | 4436 | All | 6
Z84 | Output current | ✔ | ✔ | Z | 84 | 5F12 | 55 | 1254 | 1154 | 4437 | FGI | 24
Z84 | Output current | ✔ | ✔ | Z | 84 | 5F12 | 55 | 1254 | 1154 | 4437 | RTU | 19
Z84 | Output current | ✔ | ✔ | Z | 84 | 5F12 | 55 | 1254 | 1154 | 4437 | BUS | 24
Z85 | PID feedback value | ✔ | ✔ | Z | 85 | 5F12 | 56 | 1255 | 1155 | 4438 | All | 12
Z86 | Input power | ✔ | ✔ | Z | 86 | 5F12 | 57 | 1256 | 1156 | 4439 | All | 24
Z87 | PID output | ✔ | ✔ | Z | 87 | 5F12 | 58 | 1257 | 1157 | 4440 | All | 4

## Formats
Data format [1] Integer data (positive): Minimum step 1 | [7 empty] | Back | [9 empty] | 1 | #VALUE!
(Example) When F05 (base) frequency voltage = 200V
200 = 00C8H Consequently → | [5 empty] | 00H | C8H
Data format [2] Integer data (positive/negative): Minimum step 1 | [7 empty] | Back | [9 empty] | 2 | #VALUE!
(Example) When the value is -20
-20 = FFECH Consequently → | [5 empty] | FFH | ECH
Data format [3] Decimal data (positive): Minimum step 0.1 | [7 empty] | Back | [9 empty] | 3 | #VALUE!
(Example) When F17 (gain frequency set signal) = 100.0%
100.0 x 10 = 1000 = 03E8H Consequently → | [5 empty] | 03H | E8H
Data format [4] Decimal data (positive/negative): Minimum step 0.1 | [7 empty] | Back | [9 empty] | 4 | #VALUE!
(Example) When C31 (analog input offset adjustment) = -5.0%
-5.0 x 10 = -50 = FFCEH Consequently → | [5 empty] | FFH | CEH
Data format [5] Decimal data (positive): Minimum step 0.01 | [7 empty] | Back | [9 empty] | 5 | #VALUE!
(Example) C05 (multistep frequency) = 50.25Hz ?Mini,Eco,Multi?
50.25 x 100 =5025 =13A1H Consequently → | [5 empty] | 13H | A1H
Data format [6] Decimal data (positive/negative): Minimum step 0.01 | [7 empty] | Back | [9 empty] | 6 | #VALUE!
(Example) When M07 (actual torque value) = -85.38%
-85.38 x 100 =-8538 = DEA6H Consequently → | [5 empty] | DEH | A6H
Data format [7] Decimal data (positive): Minimum step 0.001 | [7 empty] | Back | [9 empty] | 7 | #VALUE!
(Example) When F51( electronic thermal (permissible loss)) = 0.105kW
0.105 x 1000 = 105 = 0069H Consequently → | [5 empty] | 00H | 69H
Data format [8] Decimal data (positive/negative): Minimum step 0.001 | [7 empty] | Back | [9 empty] | 8 | #VALUE!
(Example) When the data is -1.234
-1.234 x 1000 = -1234 = FB2E H Consequently → | [5 empty] | FBH | 2EH
Data format [10] Alarm codes | [7 empty] | Back | [9 empty] | 10 | #VALUE!
Table 5.36 List of alarm codes
Code | Description |  |  |  |  | LED
0 | No alarm |  |  |  |  | ---
1 | Overcurrent (during acceleration) |  |  |  |  | 0c1
2 | Overcurrent (during deceleration) |  |  |  |  | 0c2
3 | Overcurrent (during constant speed operation) |  |  |  |  | 0c3
5 | Ground fault |  |  |  |  | ef
6 | Overvoltage (during acceleration) |  |  |  |  | 0u1
7 | Overvoltage (during deceleration) |  |  |  |  | 0u2
8 | Overvoltage (during constant speed operation or stopping) |  |  |  |  | 0u3
10 | Under voltage |  |  |  |  | lu
11 | Input phase loss |  |  |  |  | lin
14 | Fuse blown |  |  |  |  | fus
16 | Charging circuit fault |  |  |  |  | pbf
17 | Heat sink overheat |  |  |  |  | 0h1
18 | External alarm |  |  |  |  | 0h2
19 | Internal air overheat |  |  |  |  | 0h3
20 | Motor protection (PTC/NTC thermistor ) |  |  |  |  | 0h4
22 | Braking resistor overheat |  |  |  |  | dbh
23 | Motor overload |  |  |  |  | 0l1
24 | Motor overload: motor 2 |  |  |  |  | 0l2
25 | Inverter overload |  |  |  |  | 0lu
27 | Over speed protection |  |  |  |  | 0s
28 | PG disconnection |  |  |  |  | pg
29 | NTC disconnection error |  |  |  |  | nrb
31 | Memory error |  |  |  |  | er1
32 | Keypad communications error |  |  |  |  | er2
33 | CPU error |  |  |  |  | er3
34 | Option communications error |  |  |  |  | er4
35 | Option error |  |  |  |  | er5
36 | Run operation error |  |  |  |  | er6
37 | Tuning error |  |  |  |  | er7
38 | RS-485 communications error (communications port1) |  |  |  |  | er8
42 | Step-out detection |  |  |  |  | erd
43 | Motor selecting error |  |  |  |  | erl
44 | Motor overload: motor 3 |  |  |  |  | 0l3
45 | Motor overload: motor 4 |  |  |  |  | 0l4
46 | Output phase loss |  |  |  |  | 0pl
47 | Following error, excessive speed deviation |  |  |  |  | ere
50 | Position of magnetic pole error |  |  |  |  | erc
51 | Data save error on insufficient voltage |  |  |  |  | erf
53 | RS-485 communications error (Option/Communications port 2) |  |  |  |  | erp
54 | Hardware error |  |  |  |  | erh
55 | CAN communications failure |  |  |  |  | ert
56 | Positioning control error |  |  |  |  | ero
57 | EN circuit error |  |  |  |  | ecf
58 | PID feedback disconnection detected |  |  |  |  | cof
59 | DB transistor trouble |  |  |  |  | dba
65 | Customizable logic failure |  |  |  |  | ecl
66 | PID control 1 feedback error detection |  |  |  |  | pu1
67 | PID control 2 feedback error detection |  |  |  |  | pu2
68 | USB port transmittion error |  |  |  |  | eru
70 | Charging resistor overheat |  |  |  |  | 0h6
81 | Dry pump protection |  |  |  |  | pdr
82 | Control of maximum starts per hour |  |  |  |  | roc
83 | End of curve protection |  |  |  |  | pol
84 | Anti jam |  |  |  |  | rlo
85 | Filter clogging error |  |  |  |  | fol
91 | External PID control 1 feedback error detection |  |  |  |  | pua
92 | External PID control 2 feedback error detection |  |  |  |  | pub
93 | External PID control 3 feedback error detection |  |  |  |  | puc
100 | DC fan lock detected |  |  |  |  | fal
101 | Motor overload warning |  |  |  |  | 0l
102 | Cooling fin overheat warning |  |  |  |  | 0h
103 | Life warning |  |  |  |  | lif
104 | Command loss |  |  |  |  | ref
105 | PID warning output |  |  |  |  | pid
106 | Low torque detected |  |  |  |  | uTl
107 | Thermistor detected (PTC) |  |  |  |  | pTc
108 | Machine life (accumulated operation hours) |  |  |  |  | rTe
109 | Machine life (No. of starting times) |  |  |  |  | cnT
166 | PID control 1 warning output |  |  |  |  | pa1
167 | PID control 2 warning output |  |  |  |  | pa2
190 | Mutual operation slave inverter alarm |  |  |  |  | sla
191 | External PID control 1 warning output |  |  |  |  | paa
192 | External PID control 2 warning output |  |  |  |  | pab
193 | External PID control 3 warning output |  |  |  |  | pac
252 | Forced operation |  |  |  |  | fod
253 | Password protection |  |  |  |  | lok
254 | Simulated error |  |  |  |  | err
(Example) In the case of overvoltage (during acceleration) (0u1)
6 = 0006H Consequently→ | ? |  |  |  |  | 00H | 06H
Data format [11] Capacity code (unit: kW) | [7 empty] | Back | [9 empty] | 11 | #VALUE!
As shown in the table below, the capacity (kW) is multiplied by 100.
Table 5.37 Capacities and data
Capacity (kW) | Data | Capacity (kW) | Data | Capacity (kW) | Data
0.06 | 6 | 22 | 2200 | 280 | 28000
0.1 | 10 | 30 | 3000 | 315 | 31500
0.2 | 20 | 37 | 3700 | 355 | 35500
0.4 | 40 | 45 | 4500 | 400 | 40000
0.75 | 75 | 55 | 5500 | 450 | 45000
1.5 | 150 | 75 | 7500 | 500 | 50000
2.2 | 220 | 90 | 9000 | 550 | 55000
3.7 | 370 | 110 | 11000 | 600 | 60000
5.5 | 550 | 132 | 13200 | 650 | 60650
7.5 | 750 | 160 | 16000 | 700 | 60700
11 | 1100 | 200 | 20000 | 750 | 60750
15 | 1500 | 220 | 22000 | 800 | 60800
18.5 | 1850 | 250 | 25000 | 1000 | 61000
(Example) When the capacity is 2.2 kW | [7 empty] | Back
2.20 x 100 = 220 = 00DCH Consequently→ | [5 empty] | 00H | DCH
Data format [12] Floating point data (accel./decal. time, PID display coefficient) | [7 empty] | Back | [9 empty] | 12 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Polarity | 0 | 0 | 0 | Exponent |  | Mantissa
└ Unused ┘
Polarity: 0 →Positive (+), 1→Negative (-); Exponent: 0 to 3; Mantissa: 1 to 999
Value expressed in this form = (polarity) Mantissa x (Exponent - 2) power of 10
Value | Mantissa |  |  |  |  | Exponent | (Exp - 2) power 10
0.01 to 9.99 | 1 to 999 |  |  |  |  | 0 | 0.01
10.0 to 99.9 | 100 to 999 |  |  |  |  | 1 | 0.1
100 to 999 | 100 to 999 |  |  |  |  | 2 | 1
1000 to 9990 | 100 to 999 |  |  |  |  | 3 | 10
(Example) When F07 (acceleration time 1) = 20.0 seconds
20.0 = 200 x 0.1 => 0000 0100 1100 1000b = 04C8H
Consequently→ | ? |  |  |  |  | 04H | C8H
Data format [14] Operation command | [7 empty] | Back | [9 empty] | 14 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
RST | XR | XF | 0 | EN | X9 | X8 | X7 | X6 | X5 | X4 | X3 | X2 | X1 | REV | FWD
| (REV) | (FWD)
↑ | General-purpose input |  | Unused | EN terminal | General-purpose input | [8 empty] | FWD: Forward command
Alarm reset | [13 empty] | REV: Reverse command
(All bits are turned ON when set to 1.)
(Example) When S06 (operation command) = FWD, X1 = ON
0000 0000 0000 0101b = 0005H Consequently→ | ? |  |  |  |  | 00H | 05H
Data format [15] General-purpose output terminal | [7 empty] | Back | [9 empty] | 15 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
0 | Y3A | Y2A | Y1A | 0 | 0 | 0 | 30 | 0 | 0 | 0 | Y5 | Y4 | Y3 | Y2 | Y1
Unused | Relay option output |  |  | Unused |  |  | ↑ | Unused |  |  | General-purpose output
(Eco only)
Alarm (general-purpose output)
(All bits are turned ON when set to 1.)
(Example) When M15 (general-purpose output terminal) = Y1 = ON
0000 0000 0000 0001 b = 0001H Consequently, | ? |  |  |  |  | 00H | 01H
Data format [16] Operation status | [7 empty] | Back | [9 empty] | 16 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
BUSY | 0 | 0 | RL | ALM | DEC | ACC | IL | VL | 0 | NUV | BRK | INT | EXT | REV | FWD
(All bits are turned ON or become active when set to 1.)
Bit | Symbol | Description |  | Support |  |  |  |  | Bit | Symbol | Description |  | Support
|  |  |  | Mini | Eco | Multi | Ace | MEGA |  |  |  |  | Mini | Eco | Multi | Ace | MEGA
0 | FWD | During forward rotation |  | Y | Y | Y | Y | Y | 8 | IL | During current limiting |  | Y | Y | Y | Y | Y
1 | REV | During reverse rotation |  | Y | Y | Y | Y | Y | 9 | ACC | During acceleration |  | Y | Y | Y | Y | Y
2 | EXT | During DC braking (or during pre-exciting) |  | Y | Y | Y | Y | Y | 10 | DEC | During deceleration |  | Y | Y | Y | Y | Y
3 | INT | Inverter shut down |  | Y | Y | Y | Y | Y | 11 | ALM | Alarm relay (for any fault) |  | Y | Y | Y | Y | Y
4 | BRK | During braking (fixed to 0 for FRENIC-Mini) |  | N | Y | Y | Y | Y | 12 | RL | Communications effective |  | Y | Y | Y | Y | Y
5 | NUV | DC link circuit voltage established (0 = undervoltage) |  | Y | Y | Y | Y | Y | 13 | 0 | - |  | N | N | N | N | N
6 | TL | During torque limiting |  | N | N | Y | Y | Y | 14 | 0 | - |  | N | N | N | N | N
7 | VL | During voltage limiting |  | Y | Y | Y | Y | Y | 15 | BUSY | During function code data writing |  | Y | Y | Y | Y | Y
Data format [17] Model code | [7 empty] | Back | [9 empty] | 17 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Model |  |  |  | Generation |  |  |  | Destination |  |  |  | Input power supply
Table 5.38 List of model codes
Code | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | A | B | C | D | E
Model | VG | G | P | E | C | S | DPS | DGS | H | H | F | RHC | RHR | Lift
|  |  | AR |  |  |  | GX | AQ | (1667Hz) | (3000Hz)
Generation | 11 series | 7 series | 1 series | Eco PLUS series | 2 series
RHR A series
RHC C series
Destination | Japan | Asia | China | Europe | USA | Taiwan
(standard)
Input power supply | Single- | Single- | Three- | Three- | Three-
| phase 100V | phase 200V | phase 200V | phase 400V | phase 575V
(Example) When the inverter type is FRN1.5C 2 S-2 J
Since "model ":C is represented by code 5, "generation": 2 series by code 5, "destination": Japan (standard) by 1, and "input power supply": 3-phase 200V by 3, the model code is 5513H.
Model: Data format [19] Current value; DGS: Back |  |  |  | 19 | #VALUE!
Current values are decimal data (positive). The minimum step is 0.01 for an inverter capacity of 22kW (30HP) or less and 0.1 for an inverter capacity of 30kW (40HP) or more.
When inverter capacity is 22kW (30HP) or less, any data higher than 655A cannot be written. No correct value can be read out when a direction for write data higher than 655A is issued.
Current data is rounded down on and after the fifth digit inside the inverter. (Ex.: When a writing direction of 107.54A is issued to an inverter with a capacity of 22kW (30HP), 107.5A is written.)
(Ex.) When F11 (electronic thermal operation level) = 107.0A (40HP)
107.0×10 = 1070 = 042EH, consequently → | ? |  |  |  |  | 04H | 2EH
(Ex.) When F11 (electronic thermal operation level) = 3.60A (1HP)
3.60×10 = 360 = 0168H, consequently → | ? |  |  |  |  | 01H | 68H
Model: Data format [20] Communications error; DGS: Back |  |  |  | 20 | #VALUE!
Table 5.39 Communications error codes (common to both protocols)
Code | Description |  |  | Code | Description
71 | Checksum error, CRC error ⇒ No response |  |  | 73 | Framing error, overrun error, buffer full ⇒ No response
72 | Parity error ⇒ No response
Table 5.40 Communications error codes (for Fuji general-purpose inverter protocol)
Code | Description |  |  | Code | Description
74 | Format error |  |  | 78 | Function code error
75 | Command error |  |  | 79 | Write disabled
76 | Link priority error |  |  | 80 | Data error
77 | Function code data write right error |  |  | 81 | Error during writing
Table 5.41 Communications error codes (for RTU protocol)
Code | Description |  |  | Code | Description
1 | Improper 'FC' |  |  | 3 | Improper data (range error)
2 | Improper address (function code error) |  |  | 7 | NAK (link priority, no right, write disabled)
(Example) In case of an improper address
2 = 0002H Consequently→ | ? |  |  |  |  | 00H | 02H
Model: Data format [21] Auto tuning; DGS: Back |  |  |  | 21 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
0 | 0 | 0 | 0 | 0 | 0 | REV | FWD | Data part
Not used
When FWD is 1, this data is the forward rotation command. When REV is 1, this data is the reverse rotation command. However, if both FWD and REV are 1, the command is not effective. Both FWD and REV are 0 for reading.
(Ex.) When P04 (motor 1 automatic tuning) = 1 (forward rotation),
0000 0001 0000 0001b = 0101H Consequently→ | ? |  |  |  |  | 01H | 01H
Model: Data format [22] Frequency data; DGS: Back |  |  |  | 22 | #VALUE!
Decimal data (positive): Resolution 0.01Hz
(Ex.) When C05 (multistep frequency 1) = 50.25Hz (MEGA)
50.25×100 = 5025 = 13A1H, consequently → | ? |  |  |  |  | 13H | A1H
Model: Data format [23] Polarity + decimal data (positive); DGS: Back |  |  |  | 23 | #VALUE!
(for Fuji general-purpose inverter protocol)
Decimal data (positive): Resolution 0.01Hz
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
16-bit binary data ⇒ 4-digit ASCII code
For reverse rotation, add a negative sign (-) (ASCII) to the special additional data in the standard frame, or for forward rotation, enter a space (ASCII).
(Example) When maximum frequency = 60Hz and M09 (output frequency) = 60.00Hz (forward rotation)
60.00 x 100 = 6000 = 1770H Consequently→ | ? |  |  |  |  | 1 | 7 | 7 | 0
(Positive data is in the same data format as data format [5].)
Model: Data format [24] Floating point data; DGS: Back |  |  |  | 24 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Exponent |  | Mantissa
Exponent: 0-3 Mantissa: 1 to 9999
The value expressed by this format = the mantissa × 10^(exponent-2)
Value |  | Mantissa |  | Exponent | (Exp - 2) power 10
0.00 to 99.99 |  | 0 to 9999 |  | 0 | 0.01
100.0 to 999.9 |  | 1000 to 9999 |  | 1 | 0.1
1000 to 9999 |  | 1000 to 9999 |  | 2 | 1
10000 to 99990 |  | 1000 to 9999 |  | 3 | 10
Model: Data format [25] Capacity code (for HP); DGS: Back |  |  |  | 25 | #VALUE!
As shown in the table below, the capacity (HP) is multiplied by 100.
Code | Capacity (HP) | Code | Capacity (HP) | Code | Capacity (HP)
7 | 0.07 (reserved) | 3000 | 30 | 40000 | 400
15 | 0.15 | 4000 | 40 | 45000 | 450
(reserved)
25 | 0.25 | 5000 | 50 | 50000 | 500
50 | 0.5 | 6000 | 60 | 60000 | 600
100 | 1 | 7500 | 75 | 60700 | 700
200 | 2 | 10000 | 100 | 60750 | 750
300 | 3 | 12500 | 125 | 60800 | 800
500 | 5 | 15000 | 150 | 60850 | 850
750 | 7.5 | 17500 | 175 | 60900 | 900
1000 | 10 | 20000 | 200 | 60950 | 950
1500 | 15 | 25000 | 250 | 61000 | 1000
2000 | 20 | 30000 | 300 | 61050 | 1050
2500 | 25 | 35000 | 350
(Example) When the capacity is 3HP
3 x 100 = 300 = 012CH Consequently → | ? |  |  |  |  | 01H | 2CH
Model: Data format [29] Positive/Negative data of values converted into standard (p.u.) with 20,000; DGS: Back |  |  |  | 29 | #VALUE!
(Example) Speed (frequency) Data of ±20,000/±maximum speed (frequency)
Model: Data format [35] ROM version; DGS: Back |  |  |  | 35 | #VALUE!
Range: 0 to 9999
Model: Data format [37] Floating point data (load rotation speed, etc.); DGS: Back |  |  |  | 37 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Exponent |  | Mantissa
Exponent: 0-3 Mantissa: 1 to 9999
The value expressed by this format = the mantissa × 10^(exponent-2)
Value |  | Mantissa |  | Exponent | (Exp - 2) power 10
0.01 to 99.99 |  | 1 to 9999 |  | 0 | 0.01
100.0 to 999.9 |  | 1000 to 9999 |  | 1 | 0.1
1000 to 9999 |  | 1000 to 9999 |  | 2 | 1
10000 to 99990 |  | 1000 to 9999 |  | 3 | 10
Model: Data format [40] Alarm factor; DGS: Back |  |  |  | 40 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Alarm caused by multiple factors (1 to 5) |  |  |  | Order of alarm occurrences (1 to 5) |  |  |  | Alarm code (See Table 5.32.)
Model: Data format [41] Alarm history; DGS: Back |  |  |  | 41 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Number of serial occurrences of same alarm | [7 empty] | Alarm code (See Table 5.32.)
Indicates the content of an alarm that has occurred and the number of serial occurrence times of the alarm.
Model: Data format [43] Operation command (for I/O check); DGS: Back |  |  |  | 43 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
0 | 0 | 0 | EN2 | EN1 | X9 | X8 | X7 | X6 | X5 | X4 | X3 | X2 | X1 | REV | FWD
Unused |  |  | EN input |  | General-purpose input
(All bits are turned ON when set to 1.)
Model: Data format [44] Operation status 2; DGS: Back |  |  |  | 44 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
0 | ID2 | IDL | ID | OLP | LIFE | OH | TRY | FAN | KP | OL | IPF | SWM2 | RDY | FDT | FAR
(All bits are turned ON or become active when set to 1.)
Bit | Symbol | Description |  | Support |  | Bit | Symbol | Description |  | Support
|  |  |  | HVAC | Aqua |  |  |  |  | HVAC | Aqua
0 | FAR | Frequency arrival signal |  | Y | Y | 8 | TRY | Retry in operation |  | Y | Y
1 | FDT | Frequency level detection |  | Y | Y | 9 | OH | Heat sink overheat early warning |  | Y | Y
2 | RDY | Inverter ready to run |  | Y | Y | 10 | LIFE | Lifetime alarm |  | Y | Y
3 | SWM2 | 2nd motor is selected |  | N | N | 11 | OLP | Overload prevention control |  | Y | Y
4 | IPF | Auto-restarting after recovery of power |  | Y | Y | 12 | ID | Current detection |  | Y | Y
5 | OL | Motor overload early warning |  | Y | Y | 13 | IDL | Low level current detection |  | N | N
6 | KP | Running per keypad |  | N | N | 14 | ID2 | Current detection 2 |  | N | N
7 | FAN | Cooling fan in operation |  | Y | Y | 15 | 0 | - |  | N | N
Model: Data format [45] Floating point data; DGS: Back |  |  |  | 45 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Exponent |  | Mantissa
Exponent: 0-3 Mantissa: 1 to 9999
The value expressed by this format = the mantissa × 10^(exponent-3)
Value |  | Mantissa |  | Exponent | (Exp - 3) power 10
0.000 to 9.999 |  | 0 to 9999 |  | 0 | 0.001
10,00 to 99,99 |  | 1000 to 9999 |  | 1 | 0.01
100,0 to 999,9 |  | 1000 to 9999 |  | 2 | 0.1
1000 to 9999 |  | 1000 to 9999 |  | 3 | 1
Model: Data format [67] Operation command source codes; DGS: Back |  |  |  | 67 | #VALUE!
Code | Description |  |  | Remarks
0 | Keypad operation (Rotating direction: Depends on the terminal input) |  |  | Same with the selections for F02
1 | Terminal operation
2 | Keypad operation (CW)
3 | Keypad operation (CCW)
4 | Operation command 2
5 | Forced operation
6 to 19 | Reserved
20 | RS-485 channel1
21 | RS-485 channel2
22 | Bus option
23 | FRENIC Loader
Model: Data format [68] Frequency command source codes; DGS: Back |  |  |  | 68 | #VALUE!
Code | Description |  |  | Remarks
0 | Keypad key operation |  |  | Same with the selections for F01
1 | Voltage input (Terminal [12])
2 | Current input (Terminal [C1])
3 | Voltage input (Terminal [12]) + Current input (Terminal [C1])
4 | Inverter body volume
5 | Voltage input (Terminal [V2])
7 | UP/DOWN
8 | Keypad key operation (Balanceless, bumpless functions are activated.)
11 | Digital input (option)
12 | Pulse train input
20 | RS-485 channel1
21 | RS-485 channel2
22 | Bus option
23 | FENIC Loader
24 | Multi-step
25 | JOG
30 *1 | PID TP
31 *1 | PID analog 1
32 *1 | PID analog 2
33 *1 | PID UP/DOWN
34 *1 | PID communications command
36 *1 | PID multi-step
39 | Forced operation
*1 Under the PID dancer control, the inverter monitors the PID command source although the frequency command becomes effective as the main setting.
Model: Data format [73] Integer data (positive/negative sign bit); DGS: Back |  |  |  | 73 | #VALUE!
Resolution 1 (The high-order digit of position control data)
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Polarity | 0 | Data
Model: Data format [74] Integer data (positive): by 10 hours; DGS: Back |  |  |  | 74 | #VALUE!
(Example) M81 (Maintenance remaining hours-M1) = 12340 hours
12340 ÷10 =04D2H Consequently → | Consequently |  |  |  |  | 04H | D2H
Model: Data format [75] Integer data (positive) + [P] Exception for position control; DGS: Back |  |  |  | 75 | #VALUE!
Based on the positive integer data, setting of "-1" is permitted exceptionally. When "-1" is set on the touch probe or the loader, [P] is displayed.
Model: Data format [76] Operating status 2; DGS: Back |  |  |  | 76 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Motor classfi-cation | STO circuit check | Spare | Spare | Spare | Spare | Spare | Direction limit ON | Speed limit ON | Spare | Select motor |  | Control method
(Spares are always set to “0.”)
Signal name |  | Description |  |  |  |  | HVAC | AQUA
Control method |  | The final control method including set values and terminal conditions are shown below. |  |  |  |  | Y | Y
0 : V/f control without slip compensation
1 : Dynamic torque-vector control
2: V/f control with slip compensation
3: V/f control with speed sensor
4: Dynamic torque-vector control with speed sensor
5: Vector control without speed sensor
6: Vector control with speed sensor
10: Torque control
(vector control without speed sensor)
11: Torque control
(vector control with speed sensor)
Other than the above: Reserved
Motor selection |  | Selected motor is shown |  |  |  |  | N | N
00b: Motor1
01b: Motor2
10b: Motor3
11b: Motor4
Speed limit ON |  | “1” is set during speed limit. |  |  |  |  | N | N
Direction limit ON |  | “1” is set during direction limit. |  |  |  |  | Y | Y
Motor classfication |  | 0 : Induction motor |  |  |  |  | Y | Y
1 : Synchronous motor
STO circuit check |  | 0: Check disable |  |  |  |  | Y | Y
1: Check
Model: Data format [77] Optional input terminals; DGS: Back |  |  |  | 77 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
I16 | I15 | I14 | I13 | I12 | I11 | I10 | I9 | I8 | I7 | I6 | I5 | I4 | I3 | I2 | I1
Model: Data format [78] Optional output terminals; DGS: Back |  |  |  | 78 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | O8 | O7 | O6 | O5 | O4 | O3 | O2 | O1
Model: Data format [84] Patern operation; DGS: Back |  |  |  | 84 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Direction | 0 | ACC/DEC |  | Exponent |  | Data
(Example) C22 (Stage1) = Run time:10.0s, Rotation direction:Reverse, Acc/dec time: Time2
Rotation direction: Reverse: bit15=1
Acc/dec time: Time2: bit13=0, bit12=1
Exponent: 0.1: bit11=0, bit10=1
Run time data: 100: 64H
9000H + 0400H + 0064H = 9464H Consequently => | [5 empty] | 04H | D2H
Model: Data format [85] Clock data (Year and month); DGS: Back |  |  |  | 85 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Year (0 to 99) | [7 empty] | Month (1 to 12)
Model: Data format [86] Clock data (Day and time); DGS: Back |  |  |  | 86 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
| Date (1 to 31) | [6 empty] | Time (0 to 23)
0: Not corrected for daylight saving time
1: Corrected for daylight saving time
Model: Data format [87] Clock data (Minute and second); DGS: Back |  |  |  | 87 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Minute(0 to 59) | [7 empty] | Second (0 to 59)
Model: Data format [88] Clock data (Time and minute); DGS: Back |  |  |  | 88 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Time (0 to 23) | [7 empty] | Minute(0 to 59)
Model: Data format [89] Month and day (for scheduled operation); DGS: Back |  |  |  | 89 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Model: Operation selection; VG: Reserved; G: Format specification; P: Month; DPS: Date; RHC: Reserved; RHR: Reserved; Lift: Reserved | Reserved
[7 empty] | nth week |  |  |  |  | Day of the week
If the format specification = 0 (Month, week, and day of the week):
Item |  |  | Contents
Day of the week |  |  | 0 to 6: Monday to Sunday
nth week |  |  | 1 to 6: 1st to 6th week
7 to 31: Final week
0: Incorrect. The clock data is treated as invalid.
Month |  |  | 1 to 12: January to December
0, 13 to 15: Incorrect. The clock data is treated as invalid.
Operation Selection |  |  | Indicates whether the specified pause date for timer operation is valid or invalid.
0: Invalid (The pause date is invalid. Timer operation is performed on that day.)
1: Valid (The specified day is a timer operation pause date.)
If the format specification = 1 (Month and day):
Item |  |  | Contents
Day |  |  | 1 to 31: 1st to 31st
0: The clock data is treated as invalid.
Month |  |  | 1 to 12: January to December
0, 13 to 15: Incorrect. The clock data is treated as invalid.
Operation Selection |  |  | Indicates whether the specified pause date for timer operation is valid or invalid.
0: Invalid (The pause date is invalid. Timer operation is performed on that day.)
P: 1: Valid (The specified day is a timer operation pause date.) |  | ¡
Model: Data format [90] Month, day, time and minute (Corr. for daylight saving time); DGS: Back |  |  |  | 90 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Format specifications | Month |  |  |  | nth week |  |  | Day of the week |  |  | Hour |  |  | Minute
Day
If the format specification = 0 (Month, week, and day of the week):
Item |  |  | Contents
Minute |  |  | Indicates minutes at 15-minute intervals
0, 1, 2, 3: 0, 15, 30, 45 minutes
Hour |  |  | Indicates hours at one-hour intervals in 24-hour format.
0 to 7: 0 to 7 hours (Any other hours cannot be specified.)
Day of the week |  |  | Indicates the day of the week as a number
0 to 6: Monday to Sunday
nth week |  |  | 1 to 6: 1st to 6th week
7: Final week
0: Incorrect. The clock data is treated as invalid.
Month |  |  | 1 to 12: January to December
0, 13 to 15: Incorrect. The clock data is treated as invalid.
Format specification |  |  | 0: "Month, week and day of the week" format fixed
Model: Data format [91] Relay output signals; DGS: Back |  |  |  | 91 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
0 | 0 | 0 | 0 | Y12A | Y11A | Y10A | Y9A | Y8A | Y7A | Y6A | 0 | Y4A | Y3A | Y2A | Y1A
Model: Data format [93] Floating point data; DGS: Back |  |  |  | 93 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Exponent |  | Mantissa
Exponent: 0-3 Mantissa: 0 to 9999
The value expressed by this format = the mantissa × 10^(exponent-1)
Numeric value |  | Mantissa |  | Exponent | 10(exponent-3)
000.0 to 999.9 |  | 0 to 9999 |  | 0 | 0.1
1000 to 9999 |  | 1000 to 9999 |  | 1 | 1
10000 to 99990 |  | 1000 to 9999 |  | 2 | 10
100000 to 999900 |  | 1000 to 9999 |  | 3 | 100
Model: Data format [94] Day of the week data; DGS: Back |  |  |  | 94 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Sunday | Saturday | Friday | Thursday | Wednesday | Tuesday | Monday
Model: Data format [95] Customizable logic status; DGS: Back |  |  |  | 95 | #VALUE!
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Step enable | Reserve |  | Output species |  | Reserve |  | Input species2 |  | Reserve |  | Input species2 |  | Digital output | Digital input 2 | Digital input 1
bit0 | Digital input 1 |  | =0: OFF, =1: ON
bit1 | Digital input 2 |  | =0: OFF, =1: ON
bit2 | Digital output |  | =0: OFF, =1: ON
bit3-4 | Input species 1 |  | =0: No function assgined, =1: Digital, =2: Analog
bit7-8 | Input species 2 |  | =0: No function assgined, =1: Digital, =2: Analog
bit11-12 | Output species |  | =0: No function assgined, =1: Digital, =2: Analog
bit15 | Step enable |  | =0: Disable, =1: Enable
Destination: Japan
Input power supply: 3-phase 200V
Structure: Standard
Generation: 2 series
Model: C
Position data: 0000 to 9999
Unused
0: Positive (+), 1: Negative (-)
Unused
Run time data: 000 to 999
Unused
0: foward , 1: reverse
0: 0.01
1: 0.1
2: 1
3: 10
0: Acceleration/Deceleration Time 1
1: Acceleration/Deceleration Time 2
2: Acceleration/Deceleration Time 3
3: Acceleration/Deceleration Time 4